## SolarPanel
| Panel Width (inches) | 39.1
| Panel Cost | 427
| Panel Shipping Weight | 59.5
| Maximum Rated Power: | 280
| NOCT (deg C) | 45
| Max Power Temp Coeff | -0.44%
| Inverter Efficiency | 0.962
| Estimated Kwh Production 2005 | 233.6268
| ARA Summer Load To Offset (kw) | 3.6
| Days In Summer Season | 107
| Total Kwh's to offset | 9244.8
| Minimum Panels Required | 40
| Weight Of Panels | 2380
| Shipping Cost Of Panels | 2451.4
| Estimated Price For Panels Delivered To Pole | 19531.4
| Linear Feet For Required Panels | 130.3333
Solar data for south pole 2005 retreived from: http://amrc.ssec.wisc.edu/usap/southpole/
Formulas used in processing the data come from 'Handbook of photovoltaic science and engineering ( section 7.9.1 )
The book is available on google books here:
Handbook of photovoltaic science and engineering
WARNINGS:
PRICING DOES NOT INCLUDE CABLE, INVERTER, ENGINEERING COSTS, ETC. ONLY INCLUDES SOLAR PANELS
Estimator does not account for movement of the sun, but in comparison to the raytheon system, estimates low.
It is theorized that the light reflecting off the snow increases the irrandiance seen by the solar panels, but not by the AMRC

## Solar Data
Day | Hour | WindDir | Speed KT | Temp1C | RH1 | Current | Pres1 | Solar W/m2 | Tcell | Power Real
2005-01-01 | 0:59 | 28 | 10.4 | -24.1 | 76 | 454 | 690.9 | 454 | -9.9125 | 107.5925
2005-01-01 | 1:59 | 35 | 9.8 | -24.1 | 76 | 460 | 690.8 | 460 | -9.725 | 109.1206
2005-01-01 | 2:59 | 28 | 10.7 | -23.2 | 76 | 417 | 690.7 | 417 | -10.1687 | 98.6923
2005-01-01 | 3:59 | 31 | 9 | -23.3 | 75 | 456 | 690.7 | 456 | -9.05 | 108.551
2005-01-01 | 4:59 | 33 | 8 | -23.2 | 73 | 461 | 690.9 | 430 | -9.7625 | 101.9842
2005-01-01 | 5:59 | 31 | 7.8 | -23.7 | 73 | 461 | 691 | 323 | -13.6062 | 75.0772
2005-01-01 | 6:59 | 38 | 9.5 | -23.7 | 73 | 461 | 691.2 | 461 | -9.2937 | 109.6028
2005-01-01 | 7:59 | 37 | 9.8 | -23.8 | 72 | 461 | 691.2 | 461 | -9.3938 | 109.546
2005-01-01 | 8:59 | 39 | 11 | -23.7 | 72 | 461 | 691.2 | 458 | -9.3875 | 108.8366
2005-01-01 | 9:59 | 29 | 11.8 | -23.7 | 73 | 461 | 691.4 | 461 | -9.2937 | 109.6028
2005-01-01 | 10:59 | 17 | 11.2 | -23.8 | 73 | 456 | 691.6 | 459 | -9.4563 | 109.0354
2005-01-01 | 11:59 | 26 | 13.5 | -23.6 | 73 | 450 | 691.7 | 453 | -9.4437 | 107.6171
2005-01-01 | 12:59 | 29 | 13.1 | -23.4 | 73 | 443 | 691.9 | 447 | -9.4313 | 106.1986
2005-01-01 | 13:59 | 21 | 11.4 | -23.3 | 73 | 439 | 691.8 | 441 | -9.5188 | 104.7255
2005-01-01 | 14:59 | 23 | 12.6 | -23.1 | 72 | 434 | 691.9 | 436 | -9.475 | 103.5617
2005-01-01 | 15:59 | 22 | 13.1 | -23.1 | 73 | 430 | 692.1 | 432 | -9.6 | 102.545
2005-01-01 | 16:59 | 16 | 14.2 | -23 | 73 | 428 | 692.3 | 428 | -9.625 | 101.5824
2005-01-01 | 17:59 | 25 | 10.3 | -22.9 | 73 | 428 | 692.5 | 428 | -9.525 | 101.6351
2005-01-01 | 18:59 | 20 | 14.9 | -22.7 | 73 | 433 | 692.7 | 430 | -9.2625 | 102.2491
2005-01-01 | 19:59 | 20 | 13.2 | -22.7 | 74 | 430 | 692.8 | 431 | -9.2312 | 102.5035
2005-01-01 | 20:59 | 17 | 14.5 | -22.8 | 74 | 431 | 693.1 | 421 | -9.6438 | 99.9113
2005-01-01 | 21:59 | 16 | 14.3 | -22.8 | 74 | 434 | 693.3 | 432 | -9.3 | 102.7047
2005-01-01 | 22:59 | 14 | 13.7 | -22.8 | 74 | 440 | 693.6 | 437 | -9.1438 | 103.9776
2005-01-01 | 23:59 | 14 | 15.1 | -22.9 | 74 | 444 | 693.6 | 442 | -9.0875 | 105.1979
2005-01-02 | 0:59 | 18 | 13.1 | -23 | 74 | 451 | 693.7 | 448 | -9 | 106.6742
2005-01-02 | 1:59 | 18 | 14.7 | -23.1 | 74 | 458 | 693.9 | 456 | -8.85 | 108.6633
2005-01-02 | 2:59 | 20 | 12.6 | -23.1 | 73 | 461 | 693.9 | 460 | -8.725 | 109.6874
2005-01-02 | 3:59 | 22 | 11.5 | -23.7 | 73 | 461 | 693.9 | 458 | -9.3875 | 108.8366
2005-01-02 | 4:59 | 22 | 12.6 | -23.5 | 73 | 461 | 694.1 | 461 | -9.0938 | 109.7164
2005-01-02 | 5:59 | 18 | 11.7 | -23.5 | 73 | 435 | 694.1 | 327 | -13.2812 | 76.1379
2005-01-02 | 6:59 | 30 | 13.1 | -23.4 | 73 | 461 | 694.1 | 461 | -8.9938 | 109.7732
2005-01-02 | 7:59 | 28 | 14 | -23.3 | 72 | 461 | 694.3 | 461 | -8.8938 | 109.83
2005-01-02 | 8:59 | 28 | 12 | -23.3 | 72 | 461 | 694.4 | 458 | -8.9875 | 109.0623
2005-01-02 | 9:59 | 21 | 13.6 | -23.4 | 72 | 460 | 694.3 | 461 | -8.9938 | 109.7732
2005-01-02 | 10:59 | 26 | 12.2 | -23.4 | 72 | 455 | 694.4 | 458 | -9.0875 | 109.0059
2005-01-02 | 11:59 | 27 | 11.3 | -23.4 | 72 | 448 | 694.2 | 451 | -9.3063 | 107.2183
2005-01-02 | 12:59 | 25 | 11.2 | -23.3 | 72 | 441 | 694.2 | 444 | -9.425 | 105.4892
2005-01-02 | 13:59 | 29 | 9.8 | -23.3 | 72 | 436 | 694.4 | 439 | -9.5813 | 104.2168
2005-01-02 | 14:59 | 35 | 9.6 | -23.2 | 72 | 431 | 694.4 | 433 | -9.6687 | 102.7457
2005-01-02 | 15:59 | 33 | 7.7 | -23.4 | 72 | 427 | 694.4 | 429 | -9.9938 | 101.6248
2005-01-02 | 16:59 | 45 | 7.1 | -23.7 | 73 | 425 | 694.6 | 426 | -10.3875 | 100.7075
2005-01-02 | 17:59 | 50 | 7 | -24 | 73 | 426 | 694.7 | 425 | -10.7188 | 100.2977
2005-01-02 | 18:59 | 45 | 7.8 | -23.9 | 73 | 431 | 694.8 | 427 | -10.5563 | 100.8551
2005-01-02 | 19:59 | 42 | 9.7 | -23.8 | 74 | 428 | 694.9 | 429 | -10.3938 | 101.4134
2005-01-02 | 20:59 | 51 | 6.9 | -24 | 74 | 430 | 695 | 420 | -10.875 | 99.0368
2005-01-02 | 21:59 | 106 | 3.9 | -24.4 | 74 | 435 | 695 | 433 | -10.8688 | 102.1056
2005-01-02 | 22:59 | 43 | 6.8 | -23.9 | 74 | 440 | 695.2 | 437 | -10.2438 | 103.3853
2005-01-02 | 23:59 | 46 | 6 | -23.9 | 74 | 448 | 695.3 | 442 | -10.0875 | 104.6533
2005-01-03 | 0:59 | 100 | 3.8 | -24.4 | 73 | 456 | 695.2 | 449 | -10.3688 | 106.1551
2005-01-03 | 1:59 | 59 | 6.6 | -24.3 | 73 | 458 | 695 | 455 | -10.0813 | 107.7349
2005-01-03 | 2:59 | 41 | 8.1 | -23.9 | 74 | 461 | 695 | 461 | -9.4938 | 109.4892
2005-01-03 | 3:59 | 53 | 6.3 | -24.1 | 75 | 461 | 695.2 | 458 | -9.7875 | 108.6109
2005-01-03 | 4:59 | 43 | 8.3 | -23.7 | 74 | 461 | 695.2 | 461 | -9.2937 | 109.6028
2005-01-03 | 5:59 | 47 | 7.3 | -23.8 | 73 | 350 | 695.3 | 330 | -13.4875 | 76.7525
2005-01-03 | 6:59 | 53 | 6.6 | -23.9 | 73 | 461 | 695.4 | 461 | -9.4938 | 109.4892
2005-01-03 | 7:59 | 38 | 8.1 | -23.5 | 73 | 461 | 695.1 | 461 | -9.0938 | 109.7164
2005-01-03 | 8:59 | 51 | 7.4 | -23.4 | 73 | 461 | 695.2 | 458 | -9.0875 | 109.0059
2005-01-03 | 9:59 | 52 | 7.3 | -23.4 | 73 | 461 | 695.4 | 461 | -8.9938 | 109.7732
2005-01-03 | 10:59 | 55 | 7.3 | -23.3 | 73 | 459 | 695.4 | 458 | -8.9875 | 109.0623
2005-01-03 | 11:59 | 65 | 6.6 | -24 | 73 | 329 | 695.4 | 439 | -10.2812 | 103.8382
2005-01-03 | 12:59 | 48 | 6.7 | -21.8 | 70 | 305 | 695.4 | 327 | -11.5813 | 76.8227
2005-01-03 | 13:59 | 39 | 7.7 | -21.3 | 67 | 304 | 695.1 | 307 | -11.7063 | 72.0768
2005-01-03 | 14:59 | 26 | 10.5 | -21.2 | 66 | 321 | 695 | 316 | -11.325 | 74.3382
2005-01-03 | 15:59 | 51 | 6.6 | -21.3 | 63 | 349 | 695 | 356 | -10.175 | 84.2525
2005-01-03 | 16:59 | 37 | 6.1 | -23.1 | 75 | 423 | 695.1 | 409 | -10.3187 | 96.7233
2005-01-03 | 17:59 | 48 | 7.3 | -23.4 | 76 | 423 | 695.1 | 423 | -10.1813 | 100.1058
2005-01-03 | 18:59 | 74 | 5.4 | -24 | 76 | 429 | 695.1 | 425 | -10.7188 | 100.2977
2005-01-03 | 19:59 | 65 | 6.9 | -24.1 | 75 | 426 | 695.1 | 427 | -10.7562 | 100.7499
2005-01-03 | 20:59 | 59 | 6.7 | -24.4 | 74 | 428 | 695 | 418 | -11.3375 | 98.3271
2005-01-03 | 21:59 | 68 | 6.9 | -24.5 | 74 | 436 | 695.1 | 430 | -11.0625 | 101.2955
2005-01-03 | 22:59 | 72 | 6.2 | -24.7 | 73 | 438 | 694.9 | 435 | -11.1062 | 102.4499
2005-01-03 | 23:59 | 79 | 5.8 | -24.8 | 73 | 444 | 694.9 | 441 | -11.0188 | 103.9106
2005-01-04 | 0:59 | 69 | 7.3 | -24.8 | 72 | 450 | 694.7 | 447 | -10.8313 | 105.4276
2005-01-04 | 1:59 | 62 | 8.1 | -24.4 | 72 | 456 | 694.6 | 452 | -10.275 | 106.9166
2005-01-04 | 2:59 | 64 | 8.9 | -23.9 | 72 | 461 | 694.4 | 443 | -10.0563 | 104.9071
2005-01-04 | 3:59 | 41 | 8.8 | -21.6 | 65 | 309 | 694.2 | 348 | -10.725 | 82.1234
2005-01-04 | 4:59 | 87 | 5.2 | -21.2 | 66 | 306 | 694.2 | 310 | -11.5125 | 72.8551
2005-01-04 | 5:59 | 56 | 8.5 | -21.2 | 64 | 307 | 693.9 | 312 | -11.45 | 73.3492
2005-01-04 | 6:59 | 56 | 11.7 | -21.4 | 66 | 305 | 693.8 | 310 | -11.7125 | 72.7788
2005-01-04 | 7:59 | 58 | 10 | -20.9 | 67 | 313 | 693.6 | 309 | -11.2438 | 72.7224
2005-01-04 | 8:59 | 22 | 14.4 | -21.5 | 72 | 461 | 693.5 | 351 | -10.5312 | 82.9152
2005-01-04 | 9:59 | 38 | 9.4 | -23.3 | 73 | 456 | 693.6 | 443 | -9.4563 | 105.2346
2005-01-04 | 10:59 | 28 | 10.4 | -23.6 | 74 | 452 | 693.6 | 454 | -9.4125 | 107.8721
2005-01-04 | 11:59 | 38 | 9.2 | -23.8 | 75 | 444 | 693.6 | 442 | -9.9875 | 104.7078
2005-01-04 | 12:59 | 49 | 8.2 | -24.1 | 74 | 438 | 693.4 | 441 | -10.3187 | 104.2909
2005-01-04 | 13:59 | 73 | 6.1 | -24.7 | 74 | 433 | 693.1 | 435 | -11.1062 | 102.4499
2005-01-04 | 14:59 | 87 | 5.7 | -24.1 | 75 | 390 | 693 | 424 | -10.85 | 99.9931
2005-01-04 | 15:59 | 88 | 6 | -23.6 | 74 | 422 | 692.7 | 424 | -10.35 | 100.2543
2005-01-04 | 16:59 | 85 | 7.1 | -23.3 | 73 | 420 | 692.5 | 421 | -10.1438 | 99.6519
2005-01-04 | 17:59 | 80 | 7.2 | -23.1 | 72 | 420 | 692.5 | 420 | -9.975 | 99.5025
2005-01-04 | 18:59 | 72 | 7.7 | -22.9 | 72 | 426 | 692.5 | 422 | -9.7125 | 100.1128
2005-01-04 | 19:59 | 61 | 8.5 | -22.8 | 72 | 423 | 692.4 | 423 | -9.5813 | 100.4185
2005-01-04 | 20:59 | 51 | 9.7 | -22.9 | 72 | 425 | 692.3 | 415 | -9.9313 | 98.3404
2005-01-04 | 21:59 | 63 | 8.6 | -22.9 | 72 | 429 | 692.4 | 427 | -9.5563 | 101.3812
2005-01-04 | 22:59 | 52 | 9.4 | -22.9 | 73 | 435 | 692.4 | 432 | -9.4 | 102.6515
2005-01-04 | 23:59 | 43 | 10.5 | -22.3 | 72 | 441 | 692.5 | 438 | -8.6125 | 104.5022
2005-01-05 | 0:59 | 42 | 10.5 | -22.2 | 72 | 446 | 692.6 | 443 | -8.3562 | 105.835
2005-01-05 | 1:59 | 35 | 11.3 | -22.1 | 73 | 452 | 692.6 | 449 | -8.0687 | 107.4274
2005-01-05 | 2:59 | 36 | 13.5 | -22 | 73 | 457 | 692.5 | 454 | -7.8125 | 108.767
2005-01-05 | 3:59 | 23 | 11.3 | -22.1 | 74 | 460 | 692.6 | 455 | -7.8812 | 108.9681
2005-01-05 | 4:59 | 39 | 13.6 | -22 | 73 | 461 | 692.8 | 461 | -7.5938 | 110.5683
2005-01-05 | 5:59 | 30 | 11.4 | -22.1 | 73 | 144 | 692.9 | 326 | -11.9125 | 76.4548
2005-01-05 | 6:59 | 24 | 13.2 | -22.2 | 74 | 461 | 693.1 | 460 | -7.825 | 110.1974
2005-01-05 | 7:59 | 26 | 13.2 | -22.4 | 74 | 461 | 693.1 | 461 | -7.9938 | 110.3411
2005-01-05 | 8:59 | 19 | 11.7 | -22.4 | 74 | 459 | 693.4 | 457 | -8.1188 | 109.3133
2005-01-05 | 9:59 | 21 | 12 | -22.6 | 74 | 455 | 693.5 | 457 | -8.3187 | 109.2007
2005-01-05 | 10:59 | 25 | 11.6 | -22.6 | 74 | 449 | 693.6 | 452 | -8.475 | 107.919
2005-01-05 | 11:59 | 24 | 9 | -22.6 | 73 | 443 | 693.8 | 446 | -8.6625 | 106.3834
2005-01-05 | 12:59 | 23 | 10.1 | -22.8 | 73 | 437 | 693.8 | 440 | -9.05 | 104.7422
2005-01-05 | 13:59 | 14 | 11 | -22.8 | 74 | 431 | 693.8 | 434 | -9.2375 | 103.2136
2005-01-05 | 14:59 | 14 | 9.6 | -22.8 | 74 | 427 | 693.9 | 429 | -9.3938 | 101.9419
2005-01-05 | 15:59 | 19 | 8.1 | -22.9 | 74 | 423 | 694.1 | 425 | -9.6188 | 100.8736
2005-01-05 | 16:59 | 14 | 8.6 | -23.1 | 74 | 420 | 694.2 | 421 | -9.9437 | 99.7557
2005-01-05 | 17:59 | 16 | 8.7 | -23 | 74 | 421 | 694.2 | 420 | -9.875 | 99.5543
2005-01-05 | 18:59 | 8 | 6.3 | -23.1 | 75 | 427 | 694.5 | 423 | -9.8812 | 100.2621
2005-01-05 | 19:59 | 17 | 7.8 | -23.3 | 75 | 424 | 694.5 | 424 | -10.05 | 100.411
2005-01-05 | 20:59 | 17 | 9.4 | -23.7 | 75 | 425 | 694.6 | 415 | -10.7312 | 97.9313
2005-01-05 | 21:59 | 10 | 12 | -23.5 | 75 | 430 | 694.6 | 428 | -10.125 | 101.3187
2005-01-05 | 22:59 | 9 | 9 | -23.6 | 75 | 435 | 694.7 | 433 | -10.0687 | 102.5324
2005-01-05 | 23:59 | 11 | 8.1 | -23.8 | 75 | 441 | 695 | 438 | -10.1125 | 103.6927
2005-01-06 | 0:59 | 10 | 9.2 | -23.9 | 75 | 447 | 694.9 | 444 | -10.025 | 105.161
2005-01-06 | 1:59 | 7 | 10.5 | -23.8 | 76 | 453 | 694.8 | 450 | -9.7375 | 106.7415
2005-01-06 | 2:59 | 4 | 7.3 | -24.1 | 75 | 458 | 695 | 456 | -9.85 | 108.1015
2005-01-06 | 3:59 | 8 | 9.8 | -24.3 | 76 | 461 | 694.9 | 457 | -10.0188 | 108.2436
2005-01-06 | 4:59 | 0 | 7.6 | -24.2 | 75 | 461 | 695.2 | 461 | -9.7937 | 109.3188
2005-01-06 | 5:59 | 12 | 8.7 | -24.1 | 75 | 66 | 695.2 | 328 | -13.85 | 76.1409
2005-01-06 | 6:59 | 3 | 9.3 | -24 | 75 | 461 | 695.3 | 458 | -9.6875 | 108.6674
2005-01-06 | 7:59 | 5 | 7.3 | -23.9 | 75 | 461 | 695.5 | 461 | -9.4938 | 109.4892
2005-01-06 | 8:59 | 6 | 10 | -23.7 | 75 | 452 | 695.7 | 447 | -9.7312 | 106.0334
2005-01-06 | 9:59 | 0 | 10 | -23.5 | 74 | 461 | 695.8 | 454 | -9.3125 | 107.9281
2005-01-06 | 10:59 | 2 | 10.1 | -23 | 75 | 433 | 695.9 | 437 | -9.3438 | 103.8699
2005-01-06 | 11:59 | 0 | 8.6 | -23.3 | 75 | 374 | 696.1 | 424 | -10.05 | 100.411
2005-01-06 | 12:59 | 8 | 8.9 | -23.7 | 74 | 350 | 696.2 | 414 | -10.7625 | 97.6794
2005-01-06 | 13:59 | 6 | 11.1 | -23 | 75 | 385 | 696.2 | 421 | -9.8438 | 99.8075
2005-01-06 | 14:59 | 3 | 9.8 | -23.1 | 76 | 240 | 696.4 | 331 | -12.7562 | 77.2833
2005-01-06 | 15:59 | 3 | 8.9 | -22.5 | 76 | 403 | 696.5 | 272 | -14 | 63.0909
2005-01-06 | 16:59 | 1 | 8.3 | -22.7 | 74 | 427 | 696.7 | 440 | -8.95 | 104.7964
2005-01-06 | 17:59 | 10 | 7.6 | -22.9 | 75 | 419 | 697 | 429 | -9.4938 | 101.8891
2005-01-06 | 18:59 | 16 | 6.4 | -23.2 | 75 | 441 | 697 | 424 | -9.95 | 100.4632
2005-01-06 | 19:59 | 18 | 7.7 | -23.2 | 75 | 418 | 697 | 419 | -10.1062 | 99.1979
2005-01-06 | 20:59 | 14 | 5.4 | -23.5 | 76 | 420 | 697.6 | 410 | -10.6875 | 96.7735
2005-01-06 | 21:59 | 23 | 5.8 | -23.6 | 76 | 424 | 697.8 | 422 | -10.4125 | 99.7489
2005-01-06 | 22:59 | 25 | 5.5 | -23.7 | 76 | 429 | 697.9 | 422 | -10.5125 | 99.6969
2005-01-06 | 23:59 | 17 | 5.7 | -23.7 | 76 | 436 | 697.9 | 433 | -10.1687 | 102.479
2005-01-07 | 0:59 | 23 | 7.2 | -23.8 | 75 | 442 | 697.8 | 438 | -10.1125 | 103.6927
2005-01-07 | 1:59 | 13 | 5.6 | -23.9 | 75 | 448 | 697.9 | 445 | -9.9938 | 105.415
2005-01-07 | 2:59 | 16 | 5.6 | -24 | 76 | 454 | 697.9 | 451 | -9.9062 | 106.885
2005-01-07 | 3:59 | 19 | 8.1 | -23.9 | 76 | 461 | 697.8 | 454 | -9.7125 | 107.7043
2005-01-07 | 4:59 | 27 | 5.9 | -23.8 | 75 | 461 | 698.1 | 453 | -9.6438 | 107.5055
2005-01-07 | 5:59 | 32 | 4.5 | -23.5 | 75 | 184 | 698.2 | 344 | -12.75 | 80.3212
2005-01-07 | 6:59 | 48 | 5.1 | -24.1 | 75 | 461 | 698.1 | 398 | -11.6625 | 93.4631
2005-01-07 | 7:59 | 58 | 4.2 | -24.7 | 74 | 461 | 698.2 | 412 | -11.825 | 96.6682
2005-01-07 | 8:59 | 68 | 5.1 | -23.9 | 74 | 461 | 698.2 | 452 | -9.775 | 107.1951
2005-01-07 | 9:59 | 66 | 4.6 | -23.9 | 74 | 461 | 698.1 | 455 | -9.6813 | 107.9591
2005-01-07 | 10:59 | 64 | 5.5 | -23.8 | 73 | 444 | 698.1 | 444 | -9.925 | 105.2157
2005-01-07 | 11:59 | 69 | 5.8 | -23.9 | 73 | 437 | 698.2 | 442 | -10.0875 | 104.6533
2005-01-07 | 12:59 | 110 | 4.3 | -23.8 | 73 | 431 | 698.2 | 434 | -10.2375 | 102.6789
2005-01-07 | 13:59 | 95 | 5.7 | -24 | 74 | 425 | 698 | 428 | -10.625 | 101.0551
2005-01-07 | 14:59 | 79 | 6 | -23.8 | 73 | 421 | 697.9 | 423 | -10.5813 | 99.8973
2005-01-07 | 15:59 | 90 | 7.1 | -23.7 | 73 | 417 | 697.7 | 419 | -10.6062 | 98.9398
2005-01-07 | 16:59 | 88 | 5.6 | -23.6 | 72 | 414 | 697.5 | 415 | -10.6312 | 97.9825
2005-01-07 | 17:59 | 145 | 5.8 | -23.6 | 71 | 415 | 697.5 | 414 | -10.6625 | 97.7304
2005-01-07 | 18:59 | 136 | 7.3 | -23.5 | 70 | 421 | 697.6 | 416 | -10.5 | 98.2858
2005-01-07 | 19:59 | 116 | 10.2 | -23.6 | 70 | 417 | 697.3 | 418 | -10.5375 | 98.739
2005-01-07 | 20:59 | 94 | 8.6 | -23.4 | 70 | 419 | 697.1 | 409 | -10.6188 | 96.5721
2005-01-07 | 21:59 | 96 | 8.6 | -23.2 | 69 | 424 | 696.9 | 422 | -10.0125 | 99.9569
2005-01-07 | 22:59 | 96 | 7 | -23.2 | 68 | 430 | 696.7 | 427 | -9.8562 | 101.2234
2005-01-07 | 23:59 | 90 | 8.7 | -22.8 | 67 | 435 | 696.4 | 432 | -9.3 | 102.7047
2005-01-08 | 0:59 | 86 | 7.6 | -22.8 | 67 | 441 | 696 | 438 | -9.1125 | 104.2323
2005-01-08 | 1:59 | 107 | 6.4 | -22.6 | 67 | 447 | 695.6 | 445 | -8.6937 | 106.1277
2005-01-08 | 2:59 | 101 | 7.9 | -22.6 | 66 | 452 | 695.3 | 450 | -8.5375 | 107.4068
2005-01-08 | 3:59 | 107 | 7.9 | -22.5 | 66 | 456 | 695.1 | 451 | -8.4062 | 107.7184
2005-01-08 | 4:59 | 94 | 8.5 | -22.5 | 66 | 458 | 694.8 | 457 | -8.2188 | 109.257
2005-01-08 | 5:59 | 101 | 8.1 | -22.4 | 66 | 33 | 694.4 | 334 | -11.9625 | 78.3104
2005-01-08 | 6:59 | 102 | 9.4 | -22.2 | 65 | 460 | 694.1 | 451 | -8.1062 | 107.8851
2005-01-08 | 7:59 | 101 | 7.1 | -22.1 | 64 | 457 | 693.8 | 458 | -7.7875 | 109.7395
2005-01-08 | 8:59 | 87 | 9.9 | -22.1 | 64 | 453 | 693.5 | 451 | -8.0062 | 107.9407
2005-01-08 | 9:59 | 86 | 8.9 | -22.1 | 64 | 449 | 693.3 | 451 | -8.0062 | 107.9407
2005-01-08 | 10:59 | 91 | 9.2 | -22.5 | 65 | 417 | 693.1 | 439 | -8.7812 | 104.6495
2005-01-08 | 11:59 | 92 | 9.2 | -22.4 | 65 | 436 | 692.7 | 438 | -8.7125 | 104.4482
2005-01-08 | 12:59 | 83 | 11.2 | -22.5 | 65 | 428 | 692.4 | 432 | -9 | 102.8644
2005-01-08 | 13:59 | 65 | 9 | -22.6 | 67 | 423 | 692.1 | 425 | -9.3187 | 101.0307
2005-01-08 | 14:59 | 78 | 8.4 | -22.6 | 68 | 418 | 691.9 | 420 | -9.475 | 99.7613
2005-01-08 | 15:59 | 66 | 9.4 | -22.5 | 68 | 412 | 691.8 | 415 | -9.5312 | 98.5449
2005-01-08 | 16:59 | 70 | 8.9 | -22.6 | 70 | 410 | 691.7 | 411 | -9.7562 | 97.4811
2005-01-08 | 17:59 | 64 | 8.6 | -22.5 | 70 | 411 | 691.8 | 411 | -9.6562 | 97.5317
2005-01-08 | 18:59 | 65 | 6.6 | -22.7 | 71 | 418 | 691.9 | 413 | -9.7937 | 97.9364
2005-01-08 | 19:59 | 57 | 9.8 | -22.8 | 71 | 414 | 691.7 | 414 | -9.8625 | 98.1385
2005-01-08 | 20:59 | 48 | 8.9 | -22.8 | 72 | 416 | 691.7 | 406 | -10.1125 | 96.117
2005-01-08 | 21:59 | 57 | 7.9 | -22.9 | 72 | 420 | 691.8 | 418 | -9.8375 | 99.0995
2005-01-08 | 22:59 | 52 | 9.5 | -22.7 | 71 | 425 | 691.7 | 423 | -9.4812 | 100.4706
2005-01-08 | 23:59 | 46 | 8.1 | -22.7 | 71 | 431 | 691.8 | 428 | -9.325 | 101.7406
2005-01-09 | 0:59 | 43 | 8.9 | -22.9 | 71 | 437 | 691.8 | 434 | -9.3375 | 103.1602
2005-01-09 | 1:59 | 45 | 9.6 | -23.1 | 70 | 443 | 691.8 | 440 | -9.35 | 104.5796
2005-01-09 | 2:59 | 51 | 9.6 | -23.2 | 70 | 448 | 691.8 | 446 | -9.2625 | 106.0537
2005-01-09 | 3:59 | 48 | 9.6 | -23.4 | 71 | 452 | 691.7 | 447 | -9.4313 | 106.1986
2005-01-09 | 4:59 | 48 | 12.4 | -23.3 | 71 | 454 | 691.6 | 453 | -9.1438 | 107.7845
2005-01-09 | 5:59 | 35 | 11.2 | -23.4 | 71 | 34 | 691.7 | 330 | -13.0875 | 76.9151
2005-01-09 | 6:59 | 33 | 11 | -23.5 | 72 | 456 | 691.6 | 444 | -9.625 | 105.3798
2005-01-09 | 7:59 | 26 | 11.2 | -23.5 | 73 | 453 | 691.5 | 454 | -9.3125 | 107.9281
2005-01-09 | 8:59 | 33 | 10.6 | -23.5 | 73 | 449 | 691.7 | 447 | -9.5312 | 106.1435
2005-01-09 | 9:59 | 26 | 10.1 | -23.5 | 73 | 445 | 691.9 | 447 | -9.5312 | 106.1435
2005-01-09 | 10:59 | 38 | 9 | -23.5 | 73 | 439 | 692 | 442 | -9.6875 | 104.8711
2005-01-09 | 11:59 | 28 | 9.5 | -23.4 | 72 | 432 | 692.2 | 436 | -9.775 | 103.4005
2005-01-09 | 12:59 | 26 | 12.9 | -23.4 | 73 | 426 | 692.1 | 429 | -9.9938 | 101.6248
2005-01-09 | 13:59 | 25 | 12.7 | -23.4 | 73 | 420 | 691.9 | 423 | -10.1813 | 100.1058
2005-01-09 | 14:59 | 27 | 15.4 | -23.4 | 74 | 415 | 691.7 | 418 | -10.3375 | 98.842
2005-01-09 | 15:59 | 14 | 13.4 | -23.3 | 74 | 411 | 691.8 | 413 | -10.3938 | 97.6311
2005-01-09 | 16:59 | 22 | 12.5 | -23.5 | 74 | 409 | 692.2 | 410 | -10.6875 | 96.7735
2005-01-09 | 17:59 | 24 | 12 | -23.3 | 74 | 409 | 692.2 | 409 | -10.5188 | 96.6225
2005-01-09 | 18:59 | 25 | 11.4 | -23.4 | 74 | 416 | 692.5 | 411 | -10.5563 | 97.076
2005-01-09 | 19:59 | 22 | 11.2 | -23.5 | 75 | 412 | 692.4 | 412 | -10.625 | 97.2773
2005-01-09 | 20:59 | 12 | 12.7 | -23.8 | 76 | 414 | 692.6 | 404 | -11.175 | 95.1147
2005-01-09 | 21:59 | 14 | 10.1 | -23.8 | 76 | 419 | 692.9 | 416 | -10.8 | 98.1321
2005-01-09 | 22:59 | 14 | 11.1 | -23.9 | 76 | 424 | 693 | 421 | -10.7438 | 99.3407
2005-01-09 | 23:59 | 11 | 11.3 | -23.1 | 77 | 302 | 693.1 | 400 | -10.6 | 94.4563
2005-01-10 | 0:59 | 10 | 10.2 | -23 | 79 | 313 | 693.2 | 330 | -12.6875 | 77.0778
2005-01-10 | 1:59 | 15 | 7.8 | -23.1 | 80 | 303 | 693.4 | 323 | -13.0062 | 75.3159
2005-01-10 | 2:59 | 347 | 8.5 | -22.8 | 80 | 296 | 693.6 | 299 | -13.4563 | 69.5539
2005-01-10 | 3:59 | 353 | 9.5 | -22.1 | 80 | 295 | 693.7 | 290 | -13.0375 | 67.61
2005-01-10 | 4:59 | 5 | 8.6 | -22.3 | 79 | 320 | 694 | 303 | -12.8313 | 70.7177
2005-01-10 | 5:59 | 345 | 6.6 | -22.5 | 78 | 320 | 694.3 | 318 | -12.5625 | 74.3239
2005-01-10 | 6:59 | 339 | 6.8 | -22 | 78 | 292 | 694.5 | 311 | -12.2812 | 72.7956
2005-01-10 | 7:59 | 329 | 8.5 | -21.4 | 79 | 322 | 694.6 | 302 | -11.9625 | 70.8076
2005-01-10 | 8:59 | 328 | 7.7 | -21.5 | 80 | 299 | 694.9 | 300 | -12.125 | 70.2786
2005-01-10 | 9:59 | 318 | 6 | -21.5 | 80 | 273 | 695.4 | 281 | -12.7188 | 65.6221
2005-01-10 | 10:59 | 296 | 5.6 | -21.8 | 79 | 268 | 695.8 | 274 | -13.2375 | 63.8122
2005-01-10 | 11:59 | 307 | 2.3 | -20.6 | 80 | 277 | 696 | 273 | -12.0687 | 63.9724
2005-01-10 | 12:59 | 353 | 4.5 | -20.4 | 80 | 243 | 696.2 | 255 | -12.4313 | 59.6406
2005-01-10 | 13:59 | 10 | 5.8 | -19.9 | 80 | 261 | 696.1 | 250 | -12.0875 | 58.577
2005-01-10 | 14:59 | 0 | 7.6 | -19.5 | 81 | 251 | 696.4 | 254 | -11.5625 | 59.6786
2005-01-10 | 15:59 | 326 | 8.3 | -19.1 | 81 | 255 | 696.6 | 252 | -11.225 | 59.3134
2005-01-10 | 16:59 | 324 | 9.4 | -18.9 | 81 | 261 | 696.8 | 258 | -10.8375 | 60.8488
2005-01-10 | 17:59 | 334 | 7.1 | -18.8 | 81 | 258 | 697.1 | 258 | -10.7375 | 60.8806
2005-01-10 | 18:59 | 5 | 9 | -18.8 | 81 | 263 | 697.3 | 253 | -10.8938 | 59.6521
2005-01-10 | 19:59 | 0 | 8.3 | -18.5 | 81 | 253 | 697.5 | 258 | -10.4375 | 60.976
2005-01-10 | 20:59 | 339 | 8.3 | -18.6 | 81 | 247 | 697.9 | 251 | -10.7562 | 59.223
2005-01-10 | 21:59 | 334 | 7.3 | -18.4 | 81 | 253 | 698.2 | 250 | -10.5875 | 59.0391
2005-01-10 | 22:59 | 353 | 8.8 | -18.2 | 81 | 270 | 698.4 | 261 | -10.0437 | 61.8116
2005-01-10 | 23:59 | 341 | 10.1 | -17.9 | 82 | 271 | 698.4 | 274 | -9.3375 | 65.1288
2005-01-11 | 0:59 | 344 | 8.2 | -17.7 | 82 | 311 | 698.7 | 295 | -8.4812 | 70.4316 |  | 110.9581
2005-01-11 | 1:59 | M | M | M | M | M | M | 297 | 0 | 0 |  | BAD Data Point
2005-01-11 | 2:59 | 316 | 5.8 | -18.6 | 81 | 435 | 699.2 | 285 | -9.6937 | 67.6183
2005-01-11 | 3:59 | 349 | 5.5 | -19.6 | 80 | 320 | 699.4 | 331 | -9.2562 | 78.7106
2005-01-11 | 4:59 | 19 | 6 | -20.2 | 79 | 448 | 699.6 | 393 | -7.9188 | 94.1015
2005-01-11 | 5:59 | 350 | 5.1 | -20.6 | 79 | 74 | 699.8 | 330 | -10.2875 | 78.0535
2005-01-11 | 6:59 | M | M | M | M | M | M | 417 | 0 | 0 |  | BAD Data Point
2005-01-11 | 7:59 | 16 | 8.4 | -20.5 | 78 | 447 | 700.2 | 448 | -6.5 | 108.054
2005-01-11 | 8:59 | 31 | 7.2 | -20.6 | 78 | 455 | 700.4 | 444 | -6.725 | 106.9662
2005-01-11 | 9:59 | 46 | 6.8 | -20.4 | 78 | 461 | 700.7 | 459 | -6.0563 | 110.9581
2005-01-11 | 10:59 | 27 | 8 | -20.3 | 77 | 437 | 700.9 | 453 | -6.1437 | 109.4588
2005-01-11 | 11:59 | 30 | 10 | -20.2 | 77 | 398 | 701.2 | 412 | -7.325 | 98.9523
2005-01-11 | 12:59 | 27 | 10.2 | -20 | 76 | 441 | 701.3 | 438 | -6.3125 | 105.7433
2005-01-11 | 13:59 | 34 | 7.5 | -21 | 75 | 417 | 701.6 | 421 | -7.8438 | 100.8449
2005-01-11 | 14:59 | 26 | 9 | -20.6 | 76 | 414 | 701.8 | 414 | -7.6625 | 99.2606
2005-01-11 | 15:59 | 33 | 8.7 | -20.6 | 76 | 408 | 702 | 408 | -7.85 | 97.7278
2005-01-11 | 16:59 | 34 | 10.1 | -20.7 | 76 | 403 | 702.2 | 403 | -8.1062 | 96.4029
2005-01-11 | 17:59 | 34 | 9.2 | -20.7 | 75 | 400 | 702.5 | 401 | -8.1687 | 95.8936
2005-01-11 | 18:59 | 42 | 6.9 | -20.8 | 75 | 406 | 702.8 | 401 | -8.2688 | 95.8442
2005-01-11 | 19:59 | 37 | 7.3 | -20.8 | 75 | 402 | 702.9 | 403 | -8.2063 | 96.3532
2005-01-11 | 20:59 | 37 | 9.4 | -21.1 | 75 | 404 | 703 | 395 | -8.7562 | 94.1729
2005-01-11 | 21:59 | 30 | 10.4 | -21 | 75 | 409 | 703.3 | 406 | -8.3125 | 97.0174
2005-01-11 | 22:59 | 21 | 11.6 | -20.7 | 75 | 414 | 703.6 | 411 | -7.8563 | 98.4432
2005-01-11 | 23:59 | 14 | 11.2 | -20.7 | 75 | 420 | 703.8 | 417 | -7.6688 | 99.9766
2005-01-12 | 0:59 | 27 | 14.2 | -20.9 | 75 | 425 | 703.8 | 422 | -7.7125 | 101.1526
2005-01-12 | 1:59 | 17 | 12.4 | -21.1 | 75 | 432 | 703.9 | 429 | -7.6937 | 102.8404
2005-01-12 | 2:59 | 15 | 13 | -21 | 75 | 436 | 704.1 | 434 | -7.4375 | 104.1761
2005-01-12 | 3:59 | 30 | 8.7 | -21 | 76 | 439 | 704.4 | 435 | -7.4062 | 104.4328
2005-01-12 | 4:59 | 21 | 9.8 | -21.1 | 75 | 444 | 704.6 | 441 | -7.3187 | 105.9208
2005-01-12 | 5:59 | 17 | 11.3 | -21.1 | 76 | 100 | 704.6 | 325 | -10.9437 | 76.6081
2005-01-12 | 6:59 | 18 | 10.8 | -21.3 | 76 | 428 | 704.8 | 417 | -8.2688 | 99.6684
2005-01-12 | 7:59 | 17 | 10.2 | -20.6 | 77 | 427 | 705.1 | 436 | -6.975 | 104.9046
2005-01-12 | 8:59 | 25 | 10.1 | -20.7 | 76 | 403 | 705.3 | 423 | -7.4813 | 101.5129
2005-01-12 | 9:59 | 17 | 12.4 | -20.3 | 80 | 388 | 705.4 | 417 | -7.2687 | 100.1821
2005-01-12 | 10:59 | 26 | 10.2 | -20 | 80 | 363 | 705.7 | 403 | -7.4062 | 96.7504
2005-01-12 | 11:59 | 23 | 12.5 | -20.1 | 77 | 387 | 705.7 | 388 | -7.975 | 92.8774
2005-01-12 | 12:59 | 24 | 11.7 | -20.1 | 75 | 461 | 705.6 | 392 | -7.85 | 93.8953
2005-01-12 | 13:59 | 17 | 9.2 | -20.8 | 74 | 408 | 705.5 | 399 | -8.3313 | 95.3354
2005-01-12 | 14:59 | 27 | 10.3 | -21 | 74 | 379 | 705.5 | 392 | -8.75 | 93.4606
2005-01-12 | 15:59 | 17 | 11.8 | -21.2 | 74 | 388 | 705.5 | 386 | -9.1375 | 91.8458
2005-01-12 | 16:59 | 19 | 10.8 | -21.2 | 74 | 387 | 705.5 | 380 | -9.325 | 90.3304
2005-01-12 | 17:59 | 32 | 7.8 | -20.8 | 73 | 430 | 705.8 | 417 | -7.7687 | 99.9253
2005-01-12 | 18:59 | 39 | 7.3 | -21 | 73 | 412 | 705.8 | 396 | -8.625 | 94.4753
2005-01-12 | 19:59 | 37 | 8.5 | -21 | 73 | 412 | 705.7 | 407 | -8.2812 | 97.272
2005-01-12 | 20:59 | 55 | 6.4 | -21.5 | 72 | 398 | 705.7 | 394 | -9.1875 | 93.7251
2005-01-12 | 21:59 | 51 | 6.2 | -21.5 | 71 | 408 | 705.6 | 404 | -8.875 | 96.2595
2005-01-12 | 22:59 | 51 | 6.3 | -21.8 | 71 | 411 | 705.4 | 408 | -9.05 | 97.1246
2005-01-12 | 23:59 | 50 | 8.5 | -21.9 | 71 | 417 | 705.2 | 414 | -8.9625 | 98.5975
2005-01-13 | 0:56 | 45 | 8.4 | -21.9 | 71 | 422 | 705 | 420 | -8.775 | 100.1235
2005-01-13 | 1:59 | 40 | 8.3 | -22.1 | 71 | 428 | 704.8 | 426 | -8.7875 | 101.5472
2005-01-13 | 2:59 | 52 | 7 | -22.2 | 71 | 434 | 704.6 | 431 | -8.7312 | 102.769
2005-01-13 | 3:59 | 35 | 8 | -22.3 | 72 | 437 | 704.4 | 431 | -8.8313 | 102.7159
2005-01-13 | 4:58 | 61 | 6.1 | -22.1 | 71 | 439 | 704.2 | 438 | -8.4125 | 104.6101
2005-01-13 | 5:45 | 63 | 7.2 | -22.2 | 70 | 292 | 704.1 | 321 | -12.1687 | 75.1808
2005-01-13 | 6:59 | 58 | 5.7 | -22.5 | 71 | 407 | 703.8 | 398 | -10.0625 | 94.2476
2005-01-13 | 7:59 | 66 | 5 | -22.9 | 72 | 405 | 703.7 | 394 | -10.5875 | 93.0455
2005-01-13 | 8:59 | 63 | 5.4 | -22.7 | 71 | 404 | 703.5 | 413 | -9.7937 | 97.9364
2005-01-13 | 9:59 | 75 | 7.3 | -22.7 | 71 | 430 | 703.5 | 423 | -9.4812 | 100.4706
2005-01-13 | 10:59 | 70 | 5.8 | -22.2 | 71 | 421 | 703.2 | 427 | -8.8562 | 101.7494
2005-01-13 | 11:59 | 73 | 6.7 | -22.2 | 71 | 417 | 703 | 418 | -9.1375 | 99.46
2005-01-13 | 12:59 | 63 | 7.3 | -22.1 | 71 | 409 | 702.8 | 412 | -9.225 | 97.9879
2005-01-13 | 13:59 | 81 | 7.5 | -22.1 | 71 | 401 | 702.5 | 404 | -9.475 | 95.9608
2005-01-13 | 14:59 | 56 | 5.2 | -22 | 71 | 397 | 702.2 | 400 | -9.5 | 94.9984
2005-01-13 | 15:59 | 69 | 4.3 | -22.2 | 72 | 394 | 701.9 | 396 | -9.825 | 93.8899
2005-01-13 | 16:59 | 67 | 6.5 | -21.9 | 72 | 399 | 701.9 | 397 | -9.4938 | 94.289
2005-01-13 | 17:59 | 66 | 6.4 | -22 | 73 | 394 | 701.8 | 395 | -9.6562 | 93.7349
2005-01-13 | 18:59 | 45 | 6.1 | -21.7 | 72 | 399 | 701.6 | 394 | -9.3875 | 93.628
2005-01-13 | 19:59 | 63 | 5.5 | -21.8 | 72 | 395 | 701.5 | 395 | -9.4563 | 93.8322
2005-01-13 | 20:59 | 65 | 5.1 | -22.4 | 74 | 396 | 701.3 | 387 | -10.3063 | 91.5265
2005-01-13 | 21:59 | 60 | 5 | -22.2 | 74 | 400 | 701.3 | 398 | -9.7625 | 94.3947
2005-01-13 | 22:59 | 40 | 6.7 | -21.9 | 72 | 406 | 701.2 | 403 | -9.3063 | 95.8071
2005-01-13 | 23:59 | 58 | 5.1 | -22.3 | 72 | 411 | 701.2 | 408 | -9.55 | 96.8732
2005-01-14 | 0:59 | 62 | 6.3 | -21.7 | 71 | 417 | 700.8 | 414 | -8.7625 | 98.6995
2005-01-14 | 1:59 | 35 | 8.4 | -21.5 | 70 | 423 | 700.4 | 420 | -8.375 | 100.3304
2005-01-14 | 2:59 | 52 | 6.5 | -21.5 | 70 | 428 | 700.2 | 426 | -8.1875 | 101.8621
2005-01-14 | 3:59 | 64 | 6 | -22.2 | 73 | 431 | 700.1 | 427 | -8.8562 | 101.7494
2005-01-14 | 4:59 | 40 | 7.5 | -21.5 | 70 | 434 | 699.7 | 433 | -7.9688 | 103.6526
2005-01-14 | 5:59 | 38 | 8.7 | -21.3 | 69 | 310 | 699.6 | 330 | -10.9875 | 77.7689
2005-01-14 | 6:59 | 44 | 7.1 | -21.4 | 70 | 435 | 699.4 | 412 | -8.525 | 98.3432
2005-01-14 | 7:59 | 53 | 4.9 | -21.7 | 71 | 432 | 699.2 | 433 | -8.1687 | 103.5459
2005-01-14 | 8:59 | 57 | 4.9 | -21.8 | 71 | 428 | 699 | 427 | -8.4563 | 101.9599
2005-01-14 | 9:59 | 46 | 5.7 | -21.8 | 71 | 423 | 698.9 | 426 | -8.4875 | 101.7047
2005-01-14 | 10:59 | 35 | 7.3 | -21.7 | 71 | 418 | 698.6 | 421 | -8.5437 | 100.4818
2005-01-14 | 11:59 | 39 | 8.3 | -21.6 | 70 | 412 | 698.4 | 415 | -8.6312 | 99.005
2005-01-14 | 12:59 | 28 | 7 | -21.8 | 71 | 405 | 698.2 | 408 | -9.05 | 97.1246
2005-01-14 | 13:59 | 33 | 8.2 | -21.9 | 71 | 400 | 697.8 | 402 | -9.3375 | 95.5539
2005-01-14 | 14:59 | 44 | 5.7 | -22.3 | 72 | 395 | 697.6 | 397 | -9.8938 | 94.0933
2005-01-14 | 15:59 | 47 | 6.4 | -22.7 | 73 | 391 | 697.4 | 393 | -10.4187 | 92.8911
2005-01-14 | 16:59 | 30 | 8 | -22.6 | 73 | 389 | 697.2 | 390 | -10.4125 | 92.185
2005-01-14 | 17:59 | 15 | 9 | -22.3 | 72 | 389 | 697 | 389 | -10.1438 | 92.0774
2005-01-14 | 18:59 | 34 | 5.6 | -22.6 | 72 | 396 | 696.8 | 391 | -10.3812 | 92.4364
2005-01-14 | 19:59 | 35 | 7.2 | -22.7 | 72 | 393 | 696.6 | 393 | -10.4187 | 92.8911
2005-01-14 | 20:59 | 20 | 8.4 | -22.7 | 73 | 394 | 696.5 | 385 | -10.6687 | 90.8816
2005-01-14 | 21:59 | 114 | 3.2 | -22.9 | 73 | 399 | 696.5 | 396 | -10.525 | 93.5483
2005-01-14 | 22:59 | 44 | 5.3 | -23.7 | 74 | 405 | 696.3 | 402 | -11.1375 | 94.6624
2005-01-14 | 23:59 | 18 | 8.1 | -23 | 73 | 410 | 695.9 | 407 | -10.2812 | 96.2691
2005-01-15 | 0:59 | 20 | 6.9 | -23 | 73 | 423 | 695.9 | 416 | -10 | 98.5421
2005-01-15 | 1:59 | 60 | 4.9 | -23.6 | 73 | 411 | 695.7 | 420 | -10.475 | 99.2438
2005-01-15 | 2:59 | 20 | 7.4 | -22.9 | 73 | 429 | 695.4 | 426 | -9.5875 | 101.1274
2005-01-15 | 3:59 | 35 | 4.7 | -23.3 | 74 | 432 | 695.2 | 427 | -9.9563 | 101.1708
2005-01-15 | 4:59 | 16 | 6.4 | -23.2 | 74 | 433 | 695.1 | 432 | -9.7 | 102.4918
2005-01-15 | 5:59 | 23 | 6.3 | -23 | 74 | 382 | 695.2 | 333 | -12.5938 | 77.8169
2005-01-15 | 6:59 | 24 | 7 | -22.9 | 74 | 444 | 695.2 | 407 | -10.1813 | 96.3193
2005-01-15 | 7:59 | 22 | 7.3 | -23.2 | 73 | 439 | 695 | 410 | -10.3875 | 96.9251
2005-01-15 | 8:59 | 12 | 8 | -23 | 73 | 429 | 694.8 | 425 | -9.7188 | 100.8213
2005-01-15 | 9:59 | 15 | 6.1 | -23.3 | 73 | 422 | 694.8 | 421 | -10.1438 | 99.6519
2005-01-15 | 10:59 | 15 | 6.8 | -23.4 | 73 | 417 | 694.8 | 420 | -10.275 | 99.3473
2005-01-15 | 11:59 | 10 | 6.3 | -23.3 | 73 | 418 | 694.8 | 415 | -10.3313 | 98.1358
2005-01-15 | 12:59 | 11 | 6.8 | -23.6 | 73 | 364 | 694.5 | 396 | -11.225 | 93.2068
2005-01-15 | 13:59 | 26 | 4.9 | -23.6 | 73 | 398 | 694.4 | 395 | -11.2562 | 92.9563
2005-01-15 | 14:59 | 13 | 6.5 | -23.5 | 73 | 393 | 694.2 | 395 | -11.1562 | 93.0049
2005-01-15 | 15:59 | 30 | 5.7 | -23.7 | 74 | 389 | 694 | 390 | -11.5125 | 91.6565
2005-01-15 | 16:59 | 25 | 6.2 | -23.7 | 74 | 386 | 694 | 387 | -11.6062 | 90.9067
2005-01-15 | 17:59 | 22 | 5.9 | -23.7 | 74 | 386 | 693.8 | 386 | -11.6375 | 90.657
2005-01-15 | 18:59 | 24 | 5.4 | -23.9 | 75 | 392 | 693.6 | 387 | -11.8063 | 90.8114
2005-01-15 | 19:59 | 15 | 6.2 | -23.9 | 74 | 388 | 693.5 | 389 | -11.7438 | 91.3106
2005-01-15 | 20:59 | 50 | 4.7 | -24.3 | 75 | 390 | 693.5 | 381 | -12.3938 | 89.1277
2005-01-15 | 21:59 | 33 | 4.2 | -24.4 | 75 | 394 | 693.3 | 392 | -12.15 | 91.8186
2005-01-15 | 22:59 | 29 | 5.1 | -24.3 | 74 | 400 | 693 | 397 | -11.8938 | 93.1151
2005-01-15 | 23:59 | 14 | 5.5 | -24.3 | 74 | 405 | 692.8 | 402 | -11.7375 | 94.3652
2005-01-16 | 0:59 | 56 | 3.7 | -24.8 | 74 | 411 | 692.7 | 408 | -12.05 | 95.6166
2005-01-16 | 1:59 | 42 | 3.4 | -24.9 | 74 | 417 | 692.4 | 414 | -11.9625 | 97.0674
2005-01-16 | 2:59 | 77 | 3.5 | -25 | 74 | 422 | 692.3 | 420 | -11.875 | 98.5194
2005-01-16 | 3:59 | 41 | 3.6 | -25 | 74 | 426 | 691.9 | 421 | -11.8438 | 98.7702
2005-01-16 | 4:59 | 55 | 2.3 | -24.9 | 75 | 429 | 691.6 | 427 | -11.5563 | 100.3291
2005-01-16 | 5:59 | 14 | 2.4 | -24.6 | 75 | 369 | 691.5 | 332 | -14.225 | 76.916
2005-01-16 | 6:59 | 97 | 3.6 | -24.8 | 74 | 396 | 691.4 | 398 | -12.3625 | 93.1198
2005-01-16 | 7:59 | 82 | 0 | -24.9 | 74 | 437 | 691.1 | 391 | -12.6813 | 91.3285
2005-01-16 | 8:59 | 84 | 2 | -24.4 | 75 | 386 | 691 | 411 | -11.5563 | 96.5697
2005-01-16 | 9:59 | 80 | 1.9 | -24.3 | 75 | 392 | 690.8 | 404 | -11.675 | 94.8658
2005-01-16 | 10:59 | 71 | 0 | -24.2 | 75 | 432 | 690.6 | 428 | -10.825 | 100.9496
2005-01-16 | 11:59 | 94 | 2.6 | -24.2 | 74 | 397 | 690.2 | 418 | -11.1375 | 98.4301
2005-01-16 | 12:59 | 73 | 2.6 | -24.9 | 74 | 394 | 690.1 | 397 | -12.4938 | 92.8217
2005-01-16 | 13:59 | 55 | 2.4 | -25 | 74 | 396 | 689.9 | 392 | -12.75 | 91.5289
2005-01-16 | 14:59 | 82 | 1.6 | -24.9 | 75 | 393 | 689.6 | 391 | -12.6813 | 91.3285
2005-01-16 | 15:59 | 325 | 0.9 | -24.9 | 75 | 363 | 689.4 | 381 | -12.9938 | 88.846
2005-01-16 | 16:59 | 281 | 0 | -23.7 | 72 | 401 | 689.4 | 382 | -11.7625 | 89.6587
2005-01-16 | 17:59 | 278 | 1.4 | -23.7 | 71 | 399 | 689.3 | 366 | -12.2625 | 85.6779
2005-01-16 | 18:59 | 298 | 0 | -24.1 | 76 | 410 | 689.3 | 396 | -11.725 | 92.9629
2005-01-16 | 19:59 | 47 | 0.8 | -24.4 | 76 | 369 | 689.1 | 389 | -12.2438 | 91.071
2005-01-16 | 20:59 | 340 | 2 | -24.8 | 76 | 390 | 689.1 | 381 | -12.8938 | 88.893
2005-01-16 | 21:59 | 346 | 4.7 | -25.4 | 75 | 390 | 689.1 | 388 | -13.275 | 90.3439
2005-01-16 | 22:59 | 351 | 4.9 | -25.6 | 75 | 395 | 689.1 | 392 | -13.35 | 91.2391
2005-01-16 | 23:59 | 0 | 5.2 | -25.6 | 74 | 401 | 689.1 | 398 | -13.1625 | 92.7276
2005-01-17 | 0:59 | 51 | 1.5 | -25.7 | 75 | 407 | 689 | 403 | -13.1062 | 93.9204
2005-01-17 | 1:59 | 15 | 3.6 | -25.7 | 75 | 413 | 689 | 410 | -12.8875 | 95.6623
2005-01-17 | 2:59 | 38 | 3.2 | -25.8 | 75 | 418 | 689 | 416 | -12.8 | 97.107
2005-01-17 | 3:59 | 18 | 3.8 | -25.9 | 75 | 422 | 688.8 | 417 | -12.8688 | 97.3052
2005-01-17 | 4:59 | 31 | 3.5 | -25.8 | 75 | 425 | 689 | 423 | -12.5813 | 98.8551
2005-01-17 | 5:59 | 35 | 4.3 | -25.7 | 75 | 334 | 689 | 323 | -15.6062 | 74.2813
2005-01-17 | 6:59 | 41 | 3.8 | -25.7 | 75 | 425 | 689 | 402 | -13.1375 | 93.6719
2005-01-17 | 7:59 | 36 | 4.2 | -25.7 | 74 | 422 | 689 | 423 | -12.4812 | 98.9072
2005-01-17 | 8:59 | 28 | 4.1 | -25.6 | 74 | 418 | 689.2 | 417 | -12.5687 | 97.4593
2005-01-17 | 9:59 | 19 | 7.7 | -24.8 | 78 | 335 | 689.2 | 379 | -12.9563 | 88.3972
2005-01-17 | 10:59 | 25 | 5.9 | -24.8 | 77 | 291 | 689.3 | 315 | -14.9563 | 72.6938
2005-01-17 | 11:59 | 27 | 7.2 | -24.5 | 77 | 285 | 689.4 | 285 | -15.5938 | 65.5467
2005-01-17 | 12:59 | 44 | 5.4 | -24.4 | 76 | 272 | 689.4 | 263 | -16.1812 | 60.2966
2005-01-17 | 13:59 | 46 | 6.2 | -24.7 | 76 | 280 | 689.3 | 281 | -15.9187 | 64.5143
2005-01-17 | 14:59 | 60 | 4.5 | -25.2 | 76 | 241 | 689.2 | 263 | -16.9812 | 60.0374
2005-01-17 | 15:59 | 47 | 4.3 | -24.4 | 76 | 286 | 689 | 275 | -15.8063 | 63.1748
2005-01-17 | 16:59 | 88 | 4.4 | -24.3 | 76 | 323 | 689.1 | 291 | -15.2063 | 67.0656
2005-01-17 | 17:59 | 80 | 3.2 | -24.9 | 75 | 296 | 689 | 295 | -15.6813 | 67.8148
2005-01-17 | 18:59 | 114 | 2.2 | -24.9 | 75 | 341 | 689.1 | 360 | -13.65 | 83.658
2005-01-17 | 19:59 | 70 | 3.9 | -26 | 74 | 312 | 689.1 | 349 | -15.0938 | 80.481
2005-01-17 | 20:59 | 64 | 3.4 | -25.6 | 74 | 349 | 689.1 | 379 | -13.7562 | 88.0236
2005-01-17 | 21:59 | 65 | 3.1 | -25.9 | 74 | 395 | 689.2 | 376 | -14.15 | 87.1445
2005-01-17 | 22:59 | 60 | 3.1 | -26 | 74 | 397 | 689.2 | 389 | -13.8438 | 90.3042
2005-01-17 | 23:59 | 27 | 4.5 | -25.6 | 74 | 433 | 689 | 399 | -13.1312 | 92.9759
2005-01-18 | 0:59 | 29 | 4.7 | -25.5 | 74 | 419 | 688.9 | 405 | -12.8438 | 94.5175
2005-01-18 | 1:59 | 87 | 2.1 | -25.6 | 74 | 401 | 688.9 | 383 | -13.6312 | 89.0116
2005-01-18 | 2:59 | 38 | 3.6 | -25.8 | 74 | 372 | 688.8 | 414 | -12.8625 | 96.6083
2005-01-18 | 3:59 | 19 | 4 | -25.8 | 74 | 350 | 688.6 | 402 | -13.2375 | 93.6223
2005-01-18 | 4:59 | 25 | 4.3 | -26 | 74 | 413 | 688.6 | 365 | -14.5938 | 84.3955
2005-01-18 | 5:59 | 27 | 3.1 | -26 | 74 | 274 | 688.7 | 322 | -15.9375 | 73.9199
2005-01-18 | 6:59 | 13 | 4.6 | -26 | 74 | 425 | 688.7 | 400 | -13.5 | 93.0272
2005-01-18 | 7:59 | 82 | 2.6 | -26.4 | 73 | 358 | 688.8 | 376 | -14.65 | 86.9129
2005-01-18 | 8:59 | 20 | 4.9 | -25.4 | 75 | 361 | 688.7 | 383 | -13.4313 | 89.106
2005-01-18 | 9:59 | 20 | 4.9 | -25.6 | 74 | 421 | 688.7 | 383 | -13.6312 | 89.0116
2005-01-18 | 10:59 | 16 | 4.3 | -25.6 | 74 | 372 | 688.7 | 384 | -13.6 | 89.2588
2005-01-18 | 11:59 | 48 | 2.6 | -25.9 | 74 | 319 | 688.7 | 339 | -15.3063 | 78.0862
2005-01-18 | 12:59 | 19 | 4.3 | -25.7 | 74 | 374 | 688.5 | 357 | -14.5437 | 82.5677
2005-01-18 | 13:59 | 29 | 4.4 | -25.5 | 74 | 397 | 688.5 | 390 | -13.3125 | 90.7916
2005-01-18 | 14:59 | 25 | 4.8 | -25.2 | 74 | 402 | 688.3 | 362 | -13.8875 | 84.0168
2005-01-18 | 15:59 | 18 | 5.5 | -24.8 | 74 | 389 | 688.3 | 384 | -12.8 | 89.6373
2005-01-18 | 16:59 | 33 | 4.3 | -25.2 | 74 | 387 | 688.3 | 364 | -13.825 | 84.509
2005-01-18 | 17:59 | 25 | 4.7 | -25.7 | 73 | 301 | 688.3 | 367 | -14.2312 | 85.0218
2005-01-18 | 18:59 | 27 | 4.3 | -26.1 | 73 | 381 | 688.4 | 345 | -15.3187 | 79.4629
2005-01-18 | 19:59 | 77 | 2.5 | -26.2 | 73 | 368 | 688.5 | 363 | -14.8562 | 83.8156
2005-01-18 | 20:59 | 83 | 3.5 | -26.9 | 73 | 376 | 688.4 | 345 | -16.1187 | 79.1229
2005-01-18 | 21:59 | 55 | 4.3 | -26.7 | 73 | 383 | 688.3 | 370 | -15.1375 | 85.3037
2005-01-18 | 22:59 | 63 | 3 | -26.5 | 73 | 391 | 688.3 | 385 | -14.4688 | 89.0792
2005-01-18 | 23:59 | 54 | 2.7 | -26.1 | 73 | 361 | 688.2 | 390 | -13.9125 | 90.5033
2005-01-19 | 0:59 | 63 | 2.4 | -26 | 73 | 212 | 688.1 | 387 | -13.9062 | 89.8101
2005-01-19 | 1:59 | 88 | 2.7 | -26.8 | 73 | 255 | 687.9 | 231 | -19.5813 | 51.9925
2005-01-19 | 2:59 | 71 | 3.7 | -26 | 74 | 218 | 687.9 | 330 | -15.6875 | 75.8581
2005-01-19 | 3:59 | 75 | 2.4 | -25.5 | 75 | 332 | 687.8 | 285 | -16.5938 | 65.1956
2005-01-19 | 4:59 | 71 | 2.4 | -25.2 | 74 | 299 | 687.8 | 317 | -15.2937 | 73.0235
2005-01-19 | 5:59 | 78 | 3.2 | -26.5 | 73 | 212 | 687.9 | 236 | -19.125 | 53.2506
2005-01-19 | 6:59 | 93 | 3.7 | -27.3 | 73 | 322 | 687.8 | 244 | -19.675 | 54.8903
2005-01-19 | 7:59 | 105 | 2.2 | -25.2 | 74 | 425 | 687.6 | 410 | -12.3875 | 95.9148
2005-01-19 | 8:59 | 92 | 4 | -25.8 | 73 | 400 | 687.6 | 416 | -12.8 | 97.107
2005-01-19 | 9:59 | 95 | 3.9 | -26.4 | 72 | 412 | 687.5 | 405 | -13.7438 | 94.0684
2005-01-19 | 10:59 | 87 | 4.3 | -27.2 | 72 | 334 | 687.5 | 385 | -15.1687 | 88.7472
2005-01-19 | 11:59 | 91 | 3.8 | -26.7 | 72 | 396 | 687.3 | 388 | -14.575 | 89.7225
2005-01-19 | 12:59 | 90 | 4.1 | -27.1 | 72 | 387 | 687.3 | 376 | -15.35 | 86.5886
2005-01-19 | 13:59 | 94 | 4.3 | -27 | 72 | 397 | 687.1 | 381 | -15.0938 | 87.8603
2005-01-19 | 14:59 | 90 | 4.5 | -27 | 72 | 372 | 687.1 | 383 | -15.0312 | 88.351
2005-01-19 | 15:59 | 70 | 4 | -27 | 72 | 382 | 687 | 371 | -15.4062 | 85.4114
2005-01-19 | 16:59 | 80 | 4.7 | -27.3 | 72 | 368 | 687 | 357 | -16.1438 | 81.864
2005-01-19 | 17:59 | 77 | 3.9 | -27.5 | 72 | 371 | 687 | 368 | -16 | 84.4516
2005-01-19 | 18:59 | 82 | 3.6 | -27.4 | 72 | 384 | 687.2 | 374 | -15.7125 | 85.961
2005-01-19 | 19:59 | 71 | 4 | -27.2 | 72 | 370 | 687.3 | 379 | -15.3562 | 87.2765
2005-01-19 | 20:59 | 74 | 4.3 | -27.9 | 72 | 372 | 687.1 | 363 | -16.5562 | 83.0554
2005-01-19 | 21:59 | 69 | 4.1 | -28 | 72 | 375 | 687.2 | 373 | -16.3438 | 85.4411
2005-01-19 | 22:59 | 68 | 5.1 | -28.1 | 72 | 382 | 687.2 | 378 | -16.2875 | 86.6126
2005-01-19 | 23:59 | 65 | 4.8 | -28 | 71 | 388 | 687.2 | 385 | -15.9688 | 88.3677
2005-01-20 | 0:59 | 64 | 4.6 | -28.2 | 71 | 395 | 687.2 | 388 | -16.075 | 89.0055
2005-01-20 | 1:59 | 63 | 4.5 | -28.3 | 71 | 399 | 687.2 | 398 | -15.8625 | 91.4036
2005-01-20 | 2:59 | 55 | 4 | -28.2 | 72 | 404 | 687.2 | 402 | -15.6375 | 92.4337
2005-01-20 | 3:59 | 51 | 4.7 | -28.4 | 72 | 413 | 687.2 | 404 | -15.775 | 92.8251
2005-01-20 | 4:59 | 45 | 4.3 | -28.3 | 72 | 416 | 687.3 | 399 | -15.8313 | 91.6487
2005-01-20 | 5:59 | 55 | 3.7 | -28.1 | 72 | 154 | 687.5 | 316 | -18.225 | 71.652
2005-01-20 | 6:59 | 64 | 3.4 | -28.4 | 71 | 380 | 687.5 | 374 | -16.7125 | 85.5002
2005-01-20 | 7:59 | 50 | 4.4 | -27.8 | 71 | 439 | 687.5 | 420 | -14.675 | 97.0706
2005-01-20 | 8:59 | 54 | 4.2 | -28 | 71 | 405 | 687.5 | 420 | -14.875 | 96.9671
2005-01-20 | 9:59 | 53 | 5.3 | -28.4 | 72 | 377 | 687.5 | 358 | -17.2125 | 81.6219
2005-01-20 | 10:59 | 63 | 6 | -28.1 | 71 | 397 | 687.5 | 401 | -15.5687 | 92.2377
2005-01-20 | 11:59 | 55 | 5.1 | -28.5 | 71 | 389 | 687.6 | 390 | -16.3125 | 89.3502
2005-01-20 | 12:59 | 54 | 5.6 | -28.5 | 71 | 384 | 687.6 | 386 | -16.4375 | 88.3743
2005-01-20 | 13:59 | 45 | 4.9 | -29.2 | 70 | 378 | 687.5 | 381 | -17.2937 | 86.8277
2005-01-20 | 14:59 | 62 | 5.3 | -29.5 | 70 | 373 | 687.3 | 375 | -17.7812 | 85.2351
2005-01-20 | 15:59 | 71 | 4.3 | -29.6 | 71 | 384 | 687.3 | 369 | -18.0688 | 83.7406
2005-01-20 | 16:59 | 74 | 4.7 | -29.3 | 71 | 366 | 687.4 | 371 | -17.7063 | 84.3602
2005-01-20 | 17:59 | 79 | 5.3 | -29.5 | 71 | 369 | 687.3 | 369 | -17.9688 | 83.7861
2005-01-20 | 18:59 | 82 | 5.4 | -29.3 | 71 | 371 | 687.3 | 367 | -17.8313 | 83.3941
2005-01-20 | 19:59 | 83 | 5.5 | -29.3 | 71 | 368 | 687.2 | 367 | -17.8313 | 83.3941
2005-01-20 | 20:59 | 83 | 5.6 | -29.6 | 70 | 370 | 687.2 | 361 | -18.3188 | 81.8139
2005-01-20 | 21:59 | 76 | 4.3 | -29.8 | 70 | 373 | 687 | 372 | -18.175 | 84.3727
2005-01-20 | 22:59 | 68 | 5.8 | -29.8 | 70 | 379 | 687.1 | 376 | -18.05 | 85.3379
2005-01-20 | 23:59 | 68 | 6.5 | -29.6 | 70 | 385 | 687 | 382 | -17.6625 | 86.882
2005-01-21 | 0:59 | 59 | 6.3 | -29.6 | 70 | 392 | 687 | 388 | -17.475 | 88.3363
2005-01-21 | 1:59 | 48 | 6 | -29.4 | 71 | 396 | 686.9 | 394 | -17.0875 | 89.8904
2005-01-21 | 2:59 | 35 | 6.1 | -29.2 | 71 | 401 | 686.8 | 395 | -16.8562 | 90.2311
2005-01-21 | 3:59 | 34 | 7.7 | -29.1 | 72 | 405 | 686.8 | 401 | -16.5688 | 91.7437
2005-01-21 | 4:59 | 46 | 6.1 | -29.2 | 71 | 408 | 686.8 | 407 | -16.4812 | 93.1603
2005-01-21 | 5:59 | 40 | 7.3 | -29.2 | 71 | 192 | 686.7 | 309 | -19.5437 | 69.5627
2005-01-21 | 6:59 | 43 | 6 | -29.2 | 71 | 409 | 686.8 | 388 | -17.075 | 88.5275
2005-01-21 | 7:59 | 53 | 7 | -29.3 | 71 | 405 | 686.7 | 407 | -16.5813 | 93.1102
2005-01-21 | 8:59 | 29 | 9 | -28.6 | 72 | 404 | 686.8 | 401 | -16.0688 | 91.9907
2005-01-21 | 9:59 | 36 | 7.3 | -28.2 | 72 | 410 | 686.7 | 387 | -16.1062 | 88.7612
2005-01-21 | 10:59 | 17 | 8.1 | -28.5 | 72 | 352 | 686.7 | 393 | -16.2188 | 90.0829
2005-01-21 | 11:59 | 13 | 8.2 | -27.8 | 74 | 288 | 686.7 | 303 | -18.3313 | 68.6646
2005-01-21 | 12:59 | 11 | 8.8 | -27.5 | 74 | 302 | 686.8 | 318 | -17.5625 | 72.365
2005-01-21 | 13:59 | 3 | 7.4 | -27.5 | 74 | 301 | 686.8 | 321 | -17.4688 | 73.0848
2005-01-21 | 14:59 | 357 | 8.2 | -27 | 77 | 304 | 686.9 | 313 | -17.2188 | 71.3598
2005-01-21 | 15:59 | 15 | 4.9 | -27.5 | 75 | 270 | 687 | 305 | -17.9688 | 69.2541
2005-01-21 | 16:59 | 49 | 5.7 | -27.4 | 74 | 272 | 687.2 | 318 | -17.4625 | 72.4042
2005-01-21 | 17:59 | 21 | 5.6 | -27.2 | 74 | 270 | 687.3 | 283 | -18.3562 | 64.1236
2005-01-21 | 18:59 | 19 | 6.2 | -26.9 | 74 | 248 | 687.4 | 261 | -18.7437 | 59.0141
2005-01-21 | 19:59 | 28 | 6.7 | -27.1 | 74 | 270 | 687.5 | 262 | -18.9125 | 59.1857
2005-01-21 | 20:59 | 16 | 6.2 | -27.4 | 74 | 284 | 687.6 | 278 | -18.7125 | 62.8686
2005-01-21 | 21:59 | 14 | 7.2 | -27.4 | 74 | 315 | 687.7 | 335 | -16.9312 | 76.4941
2005-01-21 | 22:59 | 11 | 10.5 | -28.3 | 73 | 375 | 687.7 | 324 | -18.175 | 73.4859
2005-01-21 | 23:59 | 21 | 8.1 | -27.9 | 72 | 387 | 687.8 | 381 | -15.9938 | 87.4379
2005-01-22 | 0:59 | 4 | 6.4 | -27.9 | 72 | 362 | 687.9 | 362 | -16.5875 | 82.8126
2005-01-22 | 1:59 | 14 | 5.3 | -29.5 | 71 | 317 | 688 | 328 | -19.25 | 73.9588
2005-01-22 | 2:59 | 16 | 5 | -29.2 | 71 | 402 | 688.1 | 374 | -17.5125 | 85.1316
2005-01-22 | 3:59 | 17 | 5.2 | -29.8 | 71 | 401 | 688.2 | 399 | -17.3313 | 90.9113
2005-01-22 | 4:59 | 20 | 5.1 | -29.8 | 71 | 403 | 688.3 | 402 | -17.2375 | 91.6413
2005-01-22 | 5:59 | 65 | 2.7 | -29.8 | 70 | 144 | 688.4 | 303 | -20.3313 | 67.918
2005-01-22 | 6:59 | 121 | 4 | -30 | 70 | 404 | 688.5 | 383 | -18.0312 | 86.9354
2005-01-22 | 7:59 | 130 | 3.9 | -30.1 | 70 | 401 | 688.6 | 403 | -17.5063 | 91.7358
2005-01-22 | 8:59 | 134 | 4.3 | -29.9 | 70 | 398 | 688.7 | 396 | -17.525 | 90.1332
2005-01-22 | 9:59 | 121 | 4.8 | -29.7 | 70 | 393 | 688.7 | 396 | -17.325 | 90.2308
2005-01-22 | 10:59 | 112 | 5.3 | -29.7 | 70 | 388 | 688.8 | 391 | -17.4812 | 89.0163
2005-01-22 | 11:59 | 124 | 7.6 | -29.6 | 69 | 381 | 688.9 | 385 | -17.5688 | 87.6088
2005-01-22 | 12:59 | 129 | 7.9 | -29.7 | 69 | 375 | 689 | 378 | -17.8875 | 85.8675
2005-01-22 | 13:59 | 106 | 6.7 | -29.8 | 70 | 369 | 689.1 | 372 | -18.175 | 84.3727
2005-01-22 | 14:59 | 106 | 7.9 | -30 | 69 | 364 | 688.9 | 366 | -18.5625 | 82.8371
2005-01-22 | 15:59 | 112 | 6.9 | -30.2 | 69 | 360 | 689 | 362 | -18.8875 | 81.7869
2005-01-22 | 16:59 | 122 | 6.8 | -30.4 | 70 | 357 | 689.1 | 358 | -19.2125 | 80.7398
2005-01-22 | 17:59 | 113 | 7.8 | -30.3 | 70 | 357 | 689.3 | 357 | -19.1438 | 80.5445
2005-01-22 | 18:59 | 129 | 9.1 | -30.4 | 69 | 361 | 689.3 | 358 | -19.2125 | 80.7398
2005-01-22 | 19:59 | 112 | 9.3 | -30.4 | 69 | 359 | 689.2 | 360 | -19.15 | 81.2186
2005-01-22 | 20:59 | 120 | 8.9 | -30.7 | 70 | 361 | 689.2 | 353 | -19.6687 | 79.4137
2005-01-22 | 21:59 | 127 | 6.8 | -30.8 | 69 | 365 | 689.3 | 363 | -19.4563 | 81.7585
2005-01-22 | 22:59 | 122 | 7.7 | -30.7 | 69 | 370 | 689.1 | 368 | -19.2 | 83.0008
2005-01-22 | 23:59 | 115 | 8 | -30.7 | 69 | 376 | 689.1 | 373 | -19.0437 | 84.2003
2005-01-23 | 0:59 | 107 | 7.1 | -30.8 | 68 | 382 | 689.2 | 379 | -18.9563 | 85.5956
2005-01-23 | 1:59 | 110 | 6.5 | -30.9 | 67 | 387 | 689.1 | 385 | -18.8687 | 86.9922
2005-01-23 | 2:59 | 102 | 6.6 | -30.9 | 66 | 392 | 689 | 390 | -18.7125 | 88.197
2005-01-23 | 3:59 | 98 | 6.9 | -31.1 | 67 | 396 | 688.9 | 391 | -18.8813 | 88.3419
2005-01-23 | 4:59 | 94 | 6.3 | -31.1 | 65 | 398 | 689 | 397 | -18.6938 | 89.7892
2005-01-23 | 5:59 | 93 | 6.1 | -31 | 66 | 102 | 689 | 302 | -21.5625 | 67.2358
2005-01-23 | 6:59 | 95 | 5.4 | -30.9 | 67 | 400 | 688.9 | 377 | -19.1187 | 85.0684
2005-01-23 | 7:59 | 109 | 6.5 | -31.2 | 68 | 274 | 688.9 | 371 | -19.6062 | 83.4917
2005-01-23 | 8:59 | 86 | 8 | -29 | 72 | 360 | 688.9 | 309 | -19.3438 | 69.6389
2005-01-23 | 9:59 | 46 | 7.8 | -29.4 | 72 | 360 | 688.8 | 350 | -18.4625 | 79.259
2005-01-23 | 10:59 | 42 | 10.1 | -29.6 | 76 | 261 | 688.9 | 292 | -20.475 | 65.4006
2005-01-23 | 11:59 | 45 | 8.2 | -29.6 | 74 | 246 | 689 | 278 | -20.9125 | 62.1152
2005-01-23 | 12:59 | 55 | 7.4 | -30.3 | 72 | 337 | 689.2 | 338 | -19.7375 | 76.0106
2005-01-23 | 13:59 | 32 | 4.5 | -30.2 | 74 | 290 | 689.2 | 289 | -21.1687 | 64.4817
2005-01-23 | 14:59 | 53 | 3.7 | -29.6 | 73 | 283 | 689.1 | 272 | -21.1 | 60.7117
2005-01-23 | 15:59 | 100 | 4.7 | -30.4 | 71 | 355 | 689.1 | 344 | -19.65 | 77.397
2005-01-23 | 16:59 | 116 | 5 | -30.8 | 71 | 351 | 689.1 | 352 | -19.8 | 79.1319
2005-01-23 | 17:59 | 106 | 5.1 | -30.7 | 71 | 351 | 689.1 | 351 | -19.7312 | 78.9368
2005-01-23 | 18:59 | 94 | 6.2 | -30.6 | 71 | 356 | 689 | 352 | -19.6 | 79.2186
2005-01-23 | 19:59 | 96 | 5.3 | -30.7 | 71 | 353 | 688.9 | 354 | -19.6375 | 79.6523
2005-01-23 | 20:59 | 109 | 5.6 | -31 | 71 | 354 | 688.9 | 347 | -20.1562 | 77.8555
2005-01-23 | 21:59 | 101 | 4.5 | -30.8 | 71 | 358 | 688.8 | 356 | -19.675 | 80.0859
2005-01-23 | 22:59 | 105 | 5.9 | -30.8 | 71 | 364 | 688.7 | 361 | -19.5188 | 81.2802
2005-01-23 | 23:59 | 108 | 5.1 | -30.9 | 70 | 370 | 688.6 | 367 | -19.4312 | 82.6707
2005-01-24 | 0:59 | 102 | 6 | -30.8 | 70 | 375 | 688.4 | 372 | -19.175 | 83.9144
2005-01-24 | 1:59 | 98 | 7.3 | -30.8 | 69 | 381 | 688.4 | 378 | -18.9875 | 85.3552
2005-01-24 | 2:59 | 92 | 5.9 | -30.8 | 67 | 386 | 688.1 | 384 | -18.8 | 86.7987
2005-01-24 | 3:59 | 79 | 4.5 | -31 | 68 | 390 | 688.1 | 386 | -18.9375 | 87.1854
2005-01-24 | 4:59 | 89 | 7.3 | -30.7 | 66 | 392 | 687.9 | 391 | -18.4812 | 88.5346
2005-01-24 | 5:59 | 82 | 6.3 | -30.8 | 66 | 69 | 687.8 | 299 | -21.4563 | 66.607
2005-01-24 | 6:59 | 74 | 4.9 | -31 | 66 | 394 | 687.8 | 371 | -19.4062 | 83.5831
2005-01-24 | 7:59 | 80 | 5.2 | -31.1 | 66 | 391 | 687.6 | 392 | -18.85 | 88.5829
2005-01-24 | 8:59 | 52 | 3.3 | -31.2 | 66 | 387 | 687.5 | 386 | -19.1375 | 87.0903
2005-01-24 | 9:59 | 70 | 3.5 | -31.5 | 67 | 383 | 687.5 | 385 | -19.4688 | 86.7076
2005-01-24 | 10:59 | 71 | 4.3 | -31.4 | 67 | 377 | 687.4 | 380 | -19.525 | 85.5552
2005-01-24 | 11:59 | 60 | 5.3 | -31.5 | 67 | 369 | 687.4 | 374 | -19.8125 | 84.0718
2005-01-24 | 12:59 | 47 | 4.9 | -31.3 | 67 | 380 | 687.3 | 366 | -19.8625 | 82.251
2005-01-24 | 13:59 | 40 | 4.3 | -31.1 | 67 | 377 | 687.2 | 359 | -19.8813 | 80.6696
2005-01-24 | 14:59 | 19 | 5.1 | -30.5 | 70 | 347 | 687 | 334 | -20.0625 | 74.9773
2005-01-24 | 15:59 | 6 | 6.1 | -31 | 71 | 335 | 686.9 | 347 | -20.1562 | 77.8555
2005-01-24 | 16:59 | 350 | 5.2 | -32 | 72 | 338 | 686.9 | 335 | -21.5312 | 74.5956
2005-01-24 | 17:59 | 348 | 4.3 | -32.4 | 71 | 294 | 687.1 | 311 | -22.6812 | 68.8108
2005-01-24 | 18:59 | 347 | 2.3 | -32.1 | 70 | 304 | 687.1 | 315 | -22.2563 | 69.8608
2005-01-24 | 19:59 | 332 | 1.4 | -32 | 70 | 313 | 687.1 | 310 | -22.3125 | 68.7304
2005-01-24 | 20:59 | 51 | 2.1 | -32.4 | 69 | 359 | 686.9 | 340 | -21.775 | 75.6069
2005-01-24 | 21:59 | 53 | 4 | -32.2 | 69 | 303 | 686.8 | 327 | -21.9812 | 72.6329
2005-01-24 | 22:59 | 37 | 3.3 | -32.4 | 69 | 342 | 686.8 | 327 | -22.1812 | 72.5524
2005-01-24 | 23:59 | 59 | 4 | -32.6 | 69 | 366 | 686.9 | 358 | -21.4125 | 79.7695
2005-01-25 | 0:59 | 50 | 3.9 | -32.7 | 69 | 348 | 686.9 | 357 | -21.5437 | 79.4889
2005-01-25 | 1:59 | 52 | 3.3 | -32.7 | 69 | 376 | 686.8 | 362 | -21.3875 | 80.6719
2005-01-25 | 2:59 | 61 | 4 | -32.8 | 68 | 385 | 686.8 | 376 | -21.05 | 83.9482
2005-01-25 | 3:59 | 25 | 5.3 | -32.7 | 69 | 390 | 686.7 | 373 | -21.0437 | 83.2812
2005-01-25 | 4:59 | 8 | 4.8 | -33.2 | 68 | 404 | 686.6 | 379 | -21.3562 | 84.475
2005-01-25 | 5:59 | 350 | 5.2 | -33.3 | 68 | 90 | 686.7 | 301 | -23.8938 | 66.1486
2005-01-25 | 6:59 | 344 | 3.7 | -33.6 | 68 | 390 | 686.9 | 368 | -22.1 | 81.686
2005-01-25 | 7:59 | 11 | 5.5 | -33.4 | 68 | 387 | 686.9 | 379 | -21.5562 | 84.3816
2005-01-25 | 8:59 | 8 | 5.6 | -33 | 68 | 386 | 687 | 381 | -21.0938 | 85.044
2005-01-25 | 9:59 | 16 | 4.9 | -32.9 | 68 | 379 | 687 | 380 | -21.025 | 84.8529
2005-01-25 | 10:59 | 12 | 5.5 | -33 | 68 | 378 | 687.2 | 376 | -21.25 | 83.8555
2005-01-25 | 11:59 | 12 | 5.7 | -32.9 | 68 | 367 | 687.3 | 372 | -21.275 | 82.952
2005-01-25 | 12:59 | 6 | 6.1 | -32.9 | 69 | 320 | 687.4 | 359 | -21.6812 | 79.8734
2005-01-25 | 13:59 | 6 | 6.3 | -32.7 | 69 | 338 | 687.3 | 343 | -21.9812 | 76.1869
2005-01-25 | 14:59 | 24 | 4.8 | -32.2 | 69 | 349 | 687.4 | 350 | -21.2625 | 78.0516
2005-01-25 | 15:59 | 42 | 3.1 | -32.9 | 68 | 346 | 687.3 | 347 | -22.0562 | 77.0433
2005-01-25 | 16:59 | 70 | 6 | -32.7 | 68 | 318 | 687.4 | 337 | -22.1687 | 74.7763
2005-01-25 | 17:59 | 75 | 5.4 | -32.6 | 68 | 342 | 687.4 | 338 | -22.0375 | 75.0528
2005-01-25 | 18:59 | 79 | 5.2 | -32.7 | 68 | 336 | 687.5 | 341 | -22.0437 | 75.7164
2005-01-25 | 19:59 | 81 | 5.4 | -32.6 | 69 | 346 | 687.4 | 342 | -21.9125 | 75.9937
2005-01-25 | 20:59 | 88 | 6.1 | -32.6 | 69 | 342 | 687.2 | 336 | -22.1 | 74.5829
2005-01-25 | 21:59 | 77 | 5.5 | -32.5 | 69 | 350 | 687.4 | 347 | -21.6562 | 77.2143
2005-01-25 | 22:59 | 84 | 5.2 | -32.5 | 69 | 305 | 687.4 | 352 | -21.5 | 78.3946
2005-01-25 | 23:59 | 67 | 5.7 | -32.4 | 69 | 389 | 687.5 | 358 | -21.2125 | 79.8577
2005-01-26 | 0:59 | 54 | 5.8 | -31.7 | 70 | 278 | 687.5 | 361 | -20.4187 | 80.8799
2005-01-26 | 1:59 | 52 | 5.7 | -31.2 | 70 | 456 | 687.4 | 379 | -19.3562 | 85.4088
2005-01-26 | 2:59 | 47 | 6.9 | -31.9 | 69 | 333 | 687.2 | 389 | -19.7437 | 87.4766
2005-01-26 | 3:59 | 43 | 6.6 | -31.4 | 70 | 288 | 687.1 | 316 | -21.525 | 70.3673
2005-01-26 | 4:59 | 49 | 6.9 | -31.1 | 71 | 263 | 687.2 | 266 | -22.7875 | 58.8195
2005-01-26 | 5:59 | 53 | 6.3 | -32.1 | 70 | 164 | 687.2 | 242 | -24.5375 | 52.9907
2005-01-26 | 6:59 | 72 | 6.9 | -31.7 | 70 | 291 | 687.2 | 321 | -21.6687 | 71.4238
2005-01-26 | 7:59 | 66 | 6.6 | -32.2 | 69 | 355 | 687.1 | 336 | -21.7 | 74.7484
2005-01-26 | 8:59 | 74 | 6.3 | -31.7 | 70 | 380 | 687.1 | 339 | -21.1062 | 75.6638
2005-01-26 | 9:59 | 63 | 6.5 | -31.7 | 69 | 377 | 687.1 | 354 | -20.6375 | 79.2162
2005-01-26 | 10:59 | 59 | 6 | -32.4 | 68 | 347 | 687.2 | 372 | -20.775 | 83.1811
2005-01-26 | 11:59 | 61 | 4.9 | -32.6 | 67 | 362 | 687.2 | 361 | -21.3188 | 80.4796
2005-01-26 | 12:59 | 60 | 5.5 | -32.8 | 67 | 352 | 687.1 | 358 | -21.6125 | 79.6813
2005-01-26 | 13:59 | 41 | 5.9 | -33.2 | 67 | 351 | 687 | 339 | -22.6062 | 75.0373
2005-01-26 | 14:59 | 47 | 4.6 | -33 | 67 | 357 | 686.8 | 357 | -21.8438 | 79.357
2005-01-26 | 15:59 | 36 | 4.5 | -33.4 | 67 | 355 | 686.6 | 336 | -22.9 | 74.2517
2005-01-26 | 16:59 | 39 | 3.8 | -33.3 | 67 | 341 | 686.5 | 331 | -22.9563 | 73.1238
2005-01-26 | 17:59 | 54 | 2 | -33.9 | 67 | 327 | 686.4 | 325 | -23.7437 | 71.483
2005-01-26 | 18:59 | 43 | 3.5 | -33.5 | 68 | 345 | 686.3 | 328 | -23.25 | 72.3424
2005-01-26 | 19:59 | 25 | 3.3 | -33.5 | 68 | 335 | 686.2 | 338 | -22.9375 | 74.6781
2005-01-26 | 20:59 | 33 | 3.7 | -33.7 | 68 | 341 | 686 | 333 | -23.2937 | 73.4272
2005-01-26 | 21:59 | 18 | 4.2 | -33.5 | 68 | 297 | 685.8 | 342 | -22.8125 | 75.6145
2005-01-26 | 22:59 | 0 | 3.5 | -33.8 | 68 | 215 | 685.6 | 308 | -24.175 | 67.5803
2005-01-26 | 23:59 | 8 | 3.2 | -34 | 68 | 357 | 685.5 | 263 | -25.7812 | 57.1861
2005-01-27 | 0:59 | 344 | 2.7 | -33.1 | 69 | 263 | 685.4 | 338 | -22.5375 | 74.8446
2005-01-27 | 1:59 | 11 | 2.5 | -32.7 | 70 | 342 | 685.2 | 283 | -23.8562 | 62.206
2005-01-27 | 2:59 | 347 | 2.7 | -33.1 | 69 | 267 | 684.8 | 280 | -24.35 | 61.3762
2005-01-27 | 3:59 | 348 | 3 | -33.6 | 68 | 378 | 684.5 | 360 | -22.35 | 79.7993
2005-01-27 | 4:59 | 32 | 2.5 | -33.7 | 68 | 380 | 684.5 | 378 | -21.8875 | 84.0047
2005-01-27 | 5:59 | 4 | 4.5 | -34.2 | 67 | 62 | 684.3 | 275 | -25.6062 | 59.8546
2005-01-27 | 6:59 | 0 | 2.8 | -34.1 | 67 | 352 | 684.3 | 350 | -23.1625 | 77.2323
2005-01-27 | 7:59 | 16 | 2.3 | -34.2 | 67 | 378 | 684.1 | 359 | -22.9812 | 79.2985
2005-01-27 | 8:59 | 1 | 4.7 | -34.5 | 67 | 372 | 683.9 | 371 | -22.9062 | 81.9834
2005-01-27 | 9:59 | 9 | 4 | -34.5 | 67 | 357 | 683.9 | 370 | -22.9375 | 81.7482
2005-01-27 | 10:59 | 1 | 4 | -34.5 | 67 | 363 | 683.8 | 358 | -23.3125 | 78.9315
2005-01-27 | 11:59 | 3 | 5.1 | -34.1 | 67 | 356 | 683.9 | 353 | -23.0688 | 77.9351
2005-01-27 | 12:59 | 0 | 4.5 | -34.3 | 67 | 337 | 683.9 | 353 | -23.2688 | 77.8481
2005-01-27 | 13:59 | 3 | 4.9 | -34.4 | 67 | 358 | 683.9 | 336 | -23.9 | 73.8377
2005-01-27 | 14:59 | 18 | 4.4 | -34.5 | 67 | 341 | 683.8 | 338 | -23.9375 | 74.2616
2005-01-27 | 15:59 | 22 | 5.2 | -34.7 | 67 | 335 | 683.8 | 337 | -24.1687 | 73.9459
2005-01-27 | 16:59 | 17 | 4.5 | -34.6 | 67 | 332 | 683.8 | 334 | -24.1625 | 73.2902
2005-01-27 | 17:59 | 23 | 4.8 | -34.6 | 67 | 332 | 683.9 | 332 | -24.225 | 72.8258
2005-01-27 | 18:59 | 32 | 4.7 | -34.6 | 67 | 301 | 684.1 | 330 | -24.2875 | 72.3617
2005-01-27 | 19:59 | 40 | 4.9 | -34.7 | 67 | 334 | 684.2 | 334 | -24.2625 | 73.2491
2005-01-27 | 20:59 | 30 | 6.1 | -34.8 | 67 | 342 | 684.3 | 327 | -24.5813 | 71.5855
2005-01-27 | 21:59 | 29 | 5.3 | -34.9 | 67 | 336 | 684.6 | 335 | -24.4312 | 73.3987
2005-01-27 | 22:59 | 39 | 5.9 | -34.8 | 67 | 397 | 684.7 | 345 | -24.0188 | 75.7651
2005-01-27 | 23:59 | 39 | 5.3 | -34.9 | 67 | 354 | 684.9 | 343 | -24.1812 | 75.2572
2005-01-28 | 0:59 | 27 | 6.5 | -34.5 | 67 | 227 | 685.1 | 325 | -24.3438 | 71.2428
2005-01-28 | 1:59 | 35 | 7.8 | -33.3 | 69 | 296 | 685.1 | 284 | -24.425 | 62.2268
2005-01-28 | 2:59 | 56 | 8.8 | -33.1 | 69 | 270 | 685.1 | 308 | -23.475 | 67.8459
2005-01-28 | 3:59 | 48 | 7.1 | -33.1 | 69 | 269 | 685.1 | 275 | -24.5063 | 60.2273
2005-01-28 | 4:59 | 47 | 7.1 | -32.7 | 69 | 366 | 685.1 | 303 | -23.2312 | 66.8355
2005-01-28 | 5:59 | 49 | 10.5 | -32.5 | 69 | 58 | 685.3 | 287 | -23.5312 | 63.2001
2005-01-28 | 6:59 | 49 | 11 | -32.5 | 69 | 374 | 685.4 | 347 | -21.6562 | 77.2143
2005-01-28 | 7:59 | 44 | 11.7 | -32.3 | 70 | 371 | 685.5 | 373 | -20.6438 | 83.4651
2005-01-28 | 8:59 | 46 | 12.5 | -32.2 | 70 | 367 | 685.6 | 369 | -20.6687 | 82.5586
2005-01-28 | 9:59 | 58 | 10.7 | -32.4 | 70 | 363 | 685.5 | 365 | -20.9937 | 81.5175
2005-01-28 | 10:59 | 61 | 12.2 | -32.7 | 69 | 358 | 685.5 | 360 | -21.45 | 80.1985
2005-01-28 | 11:59 | 63 | 10.5 | -32.8 | 69 | 351 | 685.5 | 355 | -21.7063 | 78.9726
2005-01-28 | 12:59 | 68 | 9.1 | -33 | 68 | 345 | 685.4 | 348 | -22.125 | 77.2358
2005-01-28 | 13:59 | 68 | 12 | -32.8 | 68 | 340 | 685.3 | 342 | -22.1125 | 75.9094
2005-01-28 | 14:59 | 62 | 9.7 | -32.7 | 68 | 338 | 685.3 | 337 | -22.1687 | 74.7763
2005-01-28 | 15:59 | 62 | 12.8 | -32.5 | 68 | 339 | 685.1 | 323 | -22.4062 | 71.5753
2005-01-28 | 16:59 | 62 | 11.9 | -32.5 | 68 | 320 | 685.1 | 309 | -22.8438 | 68.3065
2005-01-28 | 17:59 | M | M | M | M | M | M | 318 | 0 | 0 |  | BAD Data Point
2005-01-28 | 19:59 | 64 | 13.2 | -31.3 | 69 | 331 | 684.8 | 333 | -20.8938 | 74.4118
2005-01-28 | 20:59 | 66 | 12.5 | -30.8 | 70 | 304 | 684.7 | 309 | -21.1438 | 68.9536
2005-01-28 | 21:59 | 49 | 14.4 | -30.9 | 70 | 285 | 684.4 | 307 | -21.3062 | 68.4459
2005-01-28 | 22:59 | 36 | 12.2 | -30.2 | 69 | 255 | 684.6 | 315 | -20.3562 | 70.5981
2005-01-28 | 23:59 | 42 | 10.1 | -30.1 | 69 | 239 | 684.5 | 281 | -21.3188 | 62.6448
2005-01-29 | 0:59 | 38 | 8.8 | -29.3 | 70 | 252 | 684.6 | 250 | -21.4875 | 55.6818
2005-01-29 | 1:59 | 37 | 9.3 | -29.1 | 70 | 392 | 684.5 | 309 | -19.4438 | 69.6008
2005-01-29 | 2:59 | 48 | 8.8 | -29.1 | 69 | 363 | 684.3 | 320 | -19.1 | 72.214
2005-01-29 | 3:59 | 45 | 8.1 | -29.2 | 70 | 322 | 684.3 | 338 | -18.6375 | 76.4686
2005-01-29 | 4:59 | 30 | 7.2 | -27.4 | 72 | 329 | 684.2 | 320 | -17.4 | 72.8842
2005-01-29 | 5:59 | 33 | 9 | -27.8 | 70 | 211 | 684.4 | 279 | -19.0813 | 62.968
2005-01-29 | 6:59 | 35 | 10 | -28.4 | 70 | 379 | 684.5 | 318 | -18.4625 | 72.0124
2005-01-29 | 7:59 | 33 | 10.6 | -29 | 69 | 343 | 684.6 | 360 | -17.75 | 81.8395
2005-01-29 | 8:59 | 23 | 12.7 | -28.6 | 70 | 309 | 684.6 | 341 | -17.9438 | 77.4388
2005-01-29 | 9:59 | 22 | 10.6 | -29.1 | 70 | 225 | 684.7 | 328 | -18.85 | 74.1204
2005-01-29 | 10:59 | 44 | 8.9 | -29.1 | 69 | 329 | 684.7 | 338 | -18.5375 | 76.5103
2005-01-29 | 11:59 | 28 | 10.5 | -28.2 | 72 | 281 | 684.8 | 294 | -19.0125 | 66.3783
2005-01-29 | 12:59 | 18 | 13.2 | -27.4 | 72 | 442 | 685 | 276 | -18.775 | 62.3951
2005-01-29 | 13:59 | 73 | 7.4 | -27.9 | 70 | 285 | 684.9 | 348 | -17.025 | 79.4224
2005-01-29 | 14:59 | 39 | 8 | -27.4 | 70 | 227 | 684.9 | 347 | -16.5562 | 79.3945
2005-01-29 | 15:59 | 32 | 10 | -27.2 | 73 | 260 | 684.7 | 236 | -19.825 | 53.047
2005-01-29 | 16:59 | 27 | 10.4 | -26.9 | 72 | 175 | 684.9 | 259 | -18.8062 | 58.542
2005-01-29 | 17:59 | 28 | 8.1 | -28.3 | 71 | 192 | 684.9 | 260 | -20.175 | 58.3295
2005-01-29 | 18:59 | 27 | 9 | -26.3 | 73 | 228 | 684.9 | 227 | -19.2063 | 51.1971
2005-01-29 | 19:59 | 17 | 10.4 | -25.3 | 73 | 230 | 684.7 | 225 | -18.2688 | 51.0059
2005-01-29 | 20:59 | 30 | 9 | -25.1 | 74 | 229 | 684.8 | 227 | -18.0063 | 51.5327
2005-01-29 | 21:59 | 29 | 7.9 | -25 | 73 | 269 | 684.9 | 225 | -17.9688 | 51.0891
2005-01-29 | 22:59 | 49 | 6.7 | -26.1 | 72 | 228 | 684.8 | 280 | -17.35 | 63.7909
2005-01-29 | 23:59 | 36 | 11.6 | -25.9 | 72 | 249 | 684.7 | 274 | -17.3375 | 62.4282
2005-01-30 | 0:59 | 56 | 8.9 | -26.8 | 71 | 253 | 684.7 | 251 | -18.9563 | 56.6873
2005-01-30 | 1:59 | 61 | 8.7 | -28.1 | 70 | 390 | 684.4 | 337 | -17.5688 | 76.6861
2005-01-30 | 2:59 | 61 | 7.8 | -28.4 | 70 | 393 | 684.4 | 325 | -18.2437 | 73.6852
2005-01-30 | 3:59 | 64 | 7.9 | -27.8 | 71 | 258 | 684.3 | 241 | -20.2688 | 54.0392
2005-01-30 | 4:59 | 42 | 4.6 | -27.9 | 70 | 238 | 684.3 | 276 | -19.275 | 62.2251
2005-01-30 | 5:59 | 54 | 8.1 | -28.3 | 71 | 156 | 684.2 | 196 | -22.175 | 43.4886
2005-01-30 | 6:59 | 59 | 9.5 | -28.5 | 69 | 350 | 684.2 | 318 | -18.5625 | 71.9733
2005-01-30 | 7:59 | 57 | 6.4 | -29.1 | 69 | 359 | 684.5 | 343 | -18.3813 | 77.7081
2005-01-30 | 8:59 | 87 | 7.4 | -30.6 | 69 | 355 | 684.4 | 356 | -19.475 | 80.1736
2005-01-30 | 9:59 | 81 | 8.1 | -31 | 68 | 350 | 684.3 | 353 | -19.9688 | 79.2833
2005-01-30 | 10:59 | 74 | 8.3 | -31.4 | 68 | 345 | 684.4 | 347 | -20.5562 | 77.6845
2005-01-30 | 11:59 | 68 | 5.5 | -30.9 | 69 | 338 | 684.2 | 342 | -20.2125 | 76.71
2005-01-30 | 12:59 | 82 | 4.5 | -31.7 | 69 | 332 | 684.3 | 335 | -21.2312 | 74.7194
2005-01-30 | 13:59 | 78 | 5.8 | -32.2 | 69 | 326 | 684.5 | 329 | -21.9187 | 73.1025
2005-01-30 | 14:59 | 68 | 5.1 | -32.2 | 69 | 321 | 684.3 | 323 | -22.1062 | 71.6947
2005-01-30 | 15:59 | 56 | 3.7 | -32.3 | 70 | 317 | 684.4 | 319 | -22.3313 | 70.7184
2005-01-30 | 16:59 | 35 | 2.2 | -32.4 | 71 | 320 | 684.4 | 313 | -22.6187 | 69.2774
2005-01-30 | 17:59 | 66 | 4.4 | -32.5 | 70 | 314 | 684.5 | 315 | -22.6562 | 69.7056
2005-01-30 | 18:59 | 337 | 0 | -32 | 72 | 318 | 684.8 | 315 | -22.1562 | 69.8996
2005-01-30 | 19:59 | 353 | 0 | -32.3 | 72 | 308 | 684.8 | 299 | -22.9563 | 66.0545
2005-01-30 | 20:59 | 354 | 2.5 | -30.7 | 74 | 320 | 685 | 315 | -20.8562 | 70.4041
2005-01-30 | 21:59 | 334 | 0 | -29.6 | 74 | 340 | 685.1 | 317 | -19.6938 | 71.3051
2005-01-30 | 22:59 | 271 | 2.2 | -30.7 | 71 | 218 | 685.2 | 300 | -21.325 | 66.8783
2005-01-30 | 23:59 | 245 | 1.7 | -32.1 | 69 | 199 | 685.2 | 273 | -23.5688 | 60.1046
2005-01-31 | 0:59 | 299 | 0 | -29.8 | 71 | 245 | 685.4 | 303 | -20.3313 | 67.918
2005-01-31 | 1:59 | 289 | 0 | -30.5 | 71 | 370 | 685.6 | 272 | -22 | 60.4101
2005-01-31 | 2:59 | 234 | 5.1 | -31 | 70 | 315 | 685.7 | 338 | -20.4375 | 75.7191
2005-01-31 | 3:59 | 221 | 4.7 | -30.1 | 71 | 260 | 685.5 | 287 | -21.1313 | 64.0487
2005-01-31 | 4:59 | 246 | 3.5 | -31.8 | 70 | 155 | 685.6 | 269 | -23.3938 | 59.2819
2005-01-31 | 5:59 | 238 | 2.8 | -31.6 | 70 | 225 | 685.8 | 200 | -25.35 | 43.5938
2005-01-31 | 6:59 | 240 | 1.7 | -31.7 | 69 | 359 | 685.7 | 315 | -21.8562 | 70.016
2005-01-31 | 7:59 | 298 | 1.5 | -31.5 | 69 | 368 | 685.8 | 358 | -20.3125 | 80.2546
2005-01-31 | 8:59 | 311 | 4.4 | -32.8 | 69 | 461 | 685.9 | 348 | -21.925 | 77.3216
2005-01-31 | 9:59 | 323 | 4.1 | -29.9 | 71 | 371 | 685.8 | 299 | -20.5562 | 66.9385
2005-01-31 | 10:59 | 317 | 4.4 | -31.5 | 70 | 238 | 685.7 | 250 | -23.6875 | 55.0042
2005-01-31 | 11:59 | 337 | 6.9 | -33.2 | 68 | 338 | 685.6 | 332 | -22.825 | 73.3984
2005-01-31 | 12:59 | 299 | 5 | -32.9 | 69 | 284 | 685.5 | 330 | -22.5875 | 73.0528
2005-01-31 | 13:59 | 324 | 5.1 | -31.9 | 70 | 351 | 685.1 | 320 | -21.9 | 71.1101
2005-01-31 | 14:59 | 342 | 6.3 | -31.3 | 70 | 165 | 684.9 | 258 | -23.2375 | 56.9074
2005-01-31 | 15:59 | 330 | 4 | -31.1 | 71 | 219 | 684.7 | 251 | -23.2563 | 55.3576
2005-01-31 | 16:59 | 291 | 3.1 | -30.9 | 70 | 315 | 684.6 | 318 | -20.9625 | 71.033
2005-01-31 | 17:59 | 325 | 2.6 | -32.8 | 68 | 333 | 684.6 | 312 | -23.05 | 68.8903
2005-01-31 | 18:59 | 334 | 4.1 | -33 | 69 | 250 | 684.5 | 279 | -24.2812 | 61.1807
2005-01-31 | 19:59 | 20 | 6.5 | -32 | 70 | 215 | 684.4 | 234 | -24.6875 | 51.1957
2005-01-31 | 20:59 | 6 | 6.4 | -33 | 69 | 295 | 684.2 | 266 | -24.6875 | 58.1968
2005-01-31 | 21:59 | 4 | 5.9 | -34 | 68 | 324 | 684.1 | 314 | -24.1875 | 68.8919
2005-01-31 | 22:59 | 3 | 5.1 | -34.1 | 68 | 323 | 683.9 | 323 | -24.0063 | 70.9386
2005-01-31 | 23:58 | 30 | 1 | -34.3 | 68 | 328 | 683.9 | 325 | -24.1438 | 71.3228
2005-02-01 | 0:59 | M | M | M | M | M | M | 328 | 0 | 0 |  | BAD Data Point
2005-02-01 | 3:59 | 99 | 6.3 | -36.6 | 66 | 324 | 683.3 | 329 | -26.3188 | 71.3191
2005-02-01 | 4:59 | 97 | 6.7 | -36.6 | 66 | 336 | 683 | 336 | -26.1 | 72.9271
2005-02-01 | 5:59 | 101 | 7.1 | -35.8 | 67 | 89 | 683 | 268 | -27.425 | 57.7305
2005-02-01 | 6:59 | 97 | 7.8 | -36 | 67 | 381 | 683 | 322 | -25.9375 | 69.9529
2005-02-01 | 7:59 | 93 | 8.4 | -34.9 | 68 | 284 | 682.8 | 300 | -25.525 | 65.326
2005-02-01 | 8:59 | 92 | 7.3 | -32.9 | 70 | 223 | 682.6 | 237 | -25.4937 | 51.6166
2005-02-01 | 9:59 | 70 | 8.9 | -30.5 | 72 | 243 | 682.5 | 233 | -23.2188 | 51.3985
2005-02-01 | 10:59 | 85 | 11.2 | -29.5 | 72 | 273 | 682.4 | 264 | -21.25 | 58.8773
2005-02-01 | 11:59 | 116 | 10 | -31.5 | 70 | 379 | 682.3 | 343 | -20.7812 | 76.6939
2005-02-01 | 12:59 | 122 | 10.4 | -31.6 | 70 | 312 | 682.2 | 322 | -21.5375 | 71.6984
2005-02-01 | 13:59 | 116 | 10.7 | -32.3 | 70 | 309 | 681.8 | 319 | -22.3313 | 70.7184
2005-02-01 | 14:59 | 116 | 10.8 | -33 | 69 | 332 | 681.5 | 318 | -23.0625 | 70.2103
2005-02-01 | 15:59 | 105 | 8.7 | -33.3 | 68 | 283 | 681.4 | 310 | -23.6125 | 68.2339
2005-02-01 | 16:59 | 115 | 9.8 | -33.4 | 68 | 293 | 681.2 | 303 | -23.9312 | 66.5742
2005-02-01 | 17:59 | 102 | 8.9 | -33.1 | 68 | 321 | 681.2 | 315 | -23.2563 | 69.4727
2005-02-01 | 18:59 | 96 | 8.9 | -32.9 | 68 | 294 | 681.1 | 307 | -23.3062 | 67.6894
2005-02-01 | 19:59 | 93 | 7 | -33 | 68 | 316 | 681 | 298 | -23.6875 | 65.5651
2005-02-01 | 20:59 | 105 | 8.8 | -33.9 | 67 | 215 | 680.9 | 265 | -25.6187 | 57.674
2005-02-01 | 21:59 | 92 | 7.3 | -33 | 67 | 202 | 680.8 | 267 | -24.6562 | 58.4259
2005-02-01 | 22:59 | 102 | 6.1 | -33 | 67 | 255 | 680.9 | 254 | -25.0625 | 55.454
2005-02-01 | 23:59 | 89 | 7 | -32.9 | 67 | 277 | 680.8 | 254 | -24.9625 | 55.4853
2005-02-02 | 0:59 | 91 | 6 | -32.9 | 67 | 230 | 680.7 | 246 | -25.2125 | 53.662
2005-02-02 | 1:59 | 74 | 4.7 | -32.2 | 67 | 271 | 680.4 | 247 | -24.4812 | 54.1027
2005-02-02 | 2:59 | 82 | 5.2 | -32.5 | 67 | 229 | 680.5 | 258 | -24.4375 | 56.526
2005-02-02 | 3:59 | 80 | 4 | -31.3 | 67 | 239 | 680.5 | 224 | -24.3 | 49.1148
2005-02-02 | 4:59 | 66 | 3.5 | -30.7 | 67 | 227 | 680.4 | 231 | -23.4812 | 50.8826
2005-02-02 | 5:59 | 80 | 2.5 | -30.6 | 67 | 204 | 680.4 | 217 | -23.8188 | 47.7086
2005-02-02 | 6:59 | 78 | 3.6 | -30.8 | 67 | 229 | 680.4 | 225 | -23.7688 | 49.4813
2005-02-02 | 7:59 | 101 | 2.8 | -30.9 | 67 | 207 | 680.5 | 221 | -23.9937 | 48.5404
2005-02-02 | 8:59 | 82 | 2.7 | -30.6 | 67 | 267 | 680.5 | 255 | -22.6313 | 56.4362
2005-02-02 | 9:59 | 88 | 1.9 | -30 | 68 | 237 | 680.4 | 232 | -22.75 | 51.3119
2005-02-02 | 10:59 | 13 | 4.2 | -29.6 | 68 | 189 | 680.4 | 216 | -22.85 | 47.7465
2005-02-02 | 11:59 | 0 | 0 | -29.6 | 68 | 225 | 680.4 | 206 | -23.1625 | 45.4567
2005-02-02 | 12:59 | 347 | 4.7 | -28.7 | 69 | 228 | 680.4 | 203 | -22.3562 | 44.9964
2005-02-02 | 13:59 | 336 | 4.1 | -30 | 69 | 251 | 680.4 | 248 | -22.25 | 55.0034
2005-02-02 | 14:59 | 313 | 2.6 | -29.2 | 70 | 338 | 680.2 | 286 | -20.2625 | 64.1317
2005-02-02 | 15:59 | 320 | 2.9 | -28.4 | 71 | 208 | 680 | 274 | -19.8375 | 61.5843
2005-02-02 | 16:59 | 314 | 3.7 | -27.3 | 71 | 215 | 679.8 | 214 | -20.6125 | 47.8944
2005-02-02 | 17:59 | 305 | 4.2 | -27.3 | 70 | 242 | 679.9 | 249 | -19.5188 | 56.0631
2005-02-02 | 18:59 | 294 | 3.7 | -28.8 | 71 | 206 | 679.8 | 249 | -21.0188 | 55.6029
2005-02-02 | 19:59 | 308 | 4.6 | -29.1 | 72 | 202 | 679.7 | 233 | -21.8188 | 51.8004
2005-02-02 | 20:59 | 305 | 2.4 | -29.9 | 73 | 225 | 679.7 | 248 | -22.15 | 55.034
2005-02-02 | 21:59 | 302 | 4.8 | -29.3 | 74 | 242 | 679.6 | 178 | -23.7375 | 39.1521
2005-02-02 | 22:59 | 332 | 6.1 | -29.3 | 72 | 163 | 679.5 | 203 | -22.9563 | 44.8463
2005-02-02 | 23:59 | 295 | 2.2 | -27.6 | 72 | 262 | 679.4 | 215 | -20.8813 | 48.047
2005-02-03 | 0:59 | 17 | 4 | -27.8 | 71 | 207 | 679.3 | 231 | -20.5813 | 51.7079
2005-02-03 | 1:59 | 101 | 0.8 | -27.9 | 71 | 305 | 679.5 | 296 | -18.65 | 66.9621
2005-02-03 | 2:59 | 31 | 5.6 | -30 | 70 | 373 | 679.4 | 314 | -20.1875 | 70.4393
2005-02-03 | 3:59 | 45 | 2.6 | -29.2 | 71 | 300 | 679.6 | 306 | -19.6375 | 68.852
2005-02-03 | 4:59 | 86 | 2.1 | -30.9 | 69 | 341 | 679.7 | 338 | -20.3375 | 75.7607
2005-02-03 | 5:59 | 119 | 6.3 | -33.1 | 68 | 196 | 679.7 | 279 | -24.3813 | 61.1463
2005-02-03 | 6:59 | 80 | 5.1 | -33.1 | 69 | 208 | 679.7 | 221 | -26.1938 | 47.9414
2005-02-03 | 7:59 | 66 | 6.1 | -34.2 | 69 | 151 | 679.8 | 207 | -27.7312 | 44.5123
2005-02-03 | 8:59 | 73 | 5.9 | -33.2 | 73 | 332 | 679.8 | 166 | -28.0125 | 35.6383
2005-02-03 | 9:59 | 71 | 6.1 | -33.6 | 70 | 329 | 679.9 | 310 | -23.9125 | 68.1193
2005-02-03 | 10:59 | 71 | 4.7 | -34 | 69 | 327 | 680 | 323 | -23.9062 | 70.9784
2005-02-03 | 11:59 | 71 | 4.4 | -34 | 68 | 317 | 680.1 | 321 | -23.9688 | 70.5142
2005-02-03 | 12:59 | 67 | 5.2 | -34.7 | 67 | 309 | 680.1 | 313 | -24.9187 | 68.3905
2005-02-03 | 13:59 | 78 | 6.6 | -35 | 66 | 303 | 680.3 | 306 | -25.4375 | 66.6655
2005-02-03 | 14:59 | 19 | 8.6 | -32.9 | 69 | 298 | 680.2 | 300 | -23.525 | 66.0652
2005-02-03 | 15:59 | 28 | 5.1 | -32.4 | 68 | 293 | 680.1 | 295 | -23.1812 | 65.089
2005-02-03 | 16:59 | 111 | 5.2 | -34.8 | 67 | 290 | 680.4 | 292 | -25.675 | 63.53
2005-02-03 | 17:59 | 85 | 6.7 | -36 | 65 | 290 | 680.7 | 290 | -26.9375 | 62.6438
2005-02-03 | 18:59 | 87 | 5.8 | -35.6 | 66 | 292 | 680.8 | 290 | -26.5375 | 62.7867
2005-02-03 | 19:59 | 70 | 8.2 | -35.5 | 66 | 291 | 681 | 292 | -26.375 | 63.2782
2005-02-03 | 20:59 | 79 | 6.7 | -35.8 | 66 | 293 | 681.3 | 286 | -26.8625 | 61.8061
2005-02-03 | 21:59 | 61 | 8.1 | -35.5 | 66 | 300 | 681.3 | 295 | -26.2812 | 63.9623
2005-02-03 | 22:59 | 70 | 6.9 | -36.3 | 65 | 304 | 681.6 | 288 | -27.3 | 62.0831
2005-02-03 | 23:59 | 39 | 8.8 | -35 | 65 | 326 | 681.7 | 291 | -25.9062 | 63.2295
2005-02-04 | 0:59 | 66 | 7.4 | -34.9 | 66 | 206 | 681.8 | 230 | -27.7125 | 49.4634
2005-02-04 | 1:59 | 50 | 10.8 | -35.1 | 66 | 220 | 682 | 202 | -28.7875 | 43.1742
2005-02-04 | 2:59 | 58 | 7.6 | -36.2 | 66 | 340 | 682 | 202 | -29.8875 | 42.9005
2005-02-04 | 3:59 | 55 | 7.5 | -32.2 | 71 | 171 | 682 | 225 | -25.1687 | 49.0932
2005-02-04 | 4:59 | 36 | 13.8 | -30.7 | 73 | 199 | 682.1 | 188 | -24.825 | 41.0997
2005-02-04 | 5:59 | 34 | 11.6 | -31.6 | 70 | 204 | 682.2 | 206 | -25.1625 | 44.9492
2005-02-04 | 6:59 | 24 | 11.1 | -31.4 | 71 | 251 | 682.4 | 220 | -24.525 | 48.1767
2005-02-04 | 7:59 | 51 | 10 | -34.3 | 67 | 330 | 682.6 | 323 | -24.2063 | 70.8591
2005-02-04 | 8:59 | 43 | 10.5 | -35 | 64 | 326 | 682.4 | 325 | -24.8438 | 71.0426
2005-02-04 | 9:59 | 37 | 9.3 | -35.3 | 63 | 317 | 682.4 | 323 | -25.2063 | 70.4611
2005-02-04 | 10:59 | 46 | 9.4 | -35.1 | 64 | 305 | 682.5 | 311 | -25.3813 | 67.7763
2005-02-04 | 11:59 | 50 | 10.1 | -34.8 | 65 | 262 | 682.7 | 296 | -25.55 | 64.4458
2005-02-04 | 12:59 | 42 | 9 | -35.1 | 64 | 251 | 682.9 | 282 | -26.2875 | 61.1415
2005-02-04 | 13:59 | 47 | 8.4 | -34 | 65 | 228 | 682.9 | 248 | -26.25 | 53.7813
2005-02-04 | 14:59 | 41 | 12.4 | -33 | 67 | 212 | 682.8 | 211 | -26.4062 | 45.7168
2005-02-04 | 15:59 | 42 | 13.1 | -32.3 | 68 | 203 | 682.7 | 205 | -25.8938 | 44.5463
2005-02-04 | 16:59 | 43 | 10.8 | -31.7 | 68 | 202 | 682.8 | 197 | -25.5437 | 42.8928
2005-02-04 | 17:59 | 46 | 11.1 | -31.5 | 68 | 202 | 682.9 | 193 | -25.4688 | 42.0397
2005-02-04 | 18:59 | 33 | 13.9 | -31.5 | 68 | 202 | 682.9 | 206 | -25.0625 | 44.9745
2005-02-04 | 19:59 | 42 | 11.3 | -32.6 | 68 | 247 | 683 | 224 | -25.6 | 48.756
2005-02-04 | 20:59 | 54 | 9.1 | -33.8 | 66 | 246 | 683 | 257 | -25.7688 | 55.8854
2005-02-04 | 21:59 | 38 | 12.7 | -32.2 | 68 | 225 | 683.1 | 233 | -24.9187 | 50.9105
2005-02-04 | 22:59 | 30 | 14.4 | -32.2 | 68 | 241 | 683 | 236 | -24.825 | 51.5933
2005-02-04 | 23:59 | 29 | 12 | -32.6 | 67 | 241 | 683.3 | 229 | -25.4438 | 49.8884
2005-02-05 | 0:59 | 31 | 14.6 | -32.9 | 67 | 235 | 683.3 | 236 | -25.525 | 51.3898
2005-02-05 | 1:59 | 29 | 12.8 | -33 | 67 | 284 | 683.2 | 236 | -25.625 | 51.3607
2005-02-05 | 2:59 | 31 | 11.2 | -32.8 | 67 | 229 | 683.3 | 207 | -26.3313 | 44.8693
2005-02-05 | 3:59 | 45 | 12.1 | -33.4 | 66 | 308 | 683.3 | 288 | -24.4 | 63.1121
2005-02-05 | 4:59 | 43 | 12.9 | -33.7 | 66 | 293 | 683.4 | 296 | -24.45 | 64.847
2005-02-05 | 5:59 | 45 | 13.6 | -33.6 | 66 | 198 | 683.5 | 234 | -26.2875 | 50.7344
2005-02-05 | 6:59 | 33 | 15.4 | -34 | 65 | 309 | 683.6 | 276 | -25.375 | 60.1509
2005-02-05 | 7:59 | 19 | 15.1 | -33.6 | 66 | 284 | 683.7 | 294 | -24.4125 | 64.4224
2005-02-05 | 8:59 | 24 | 14.3 | -33.7 | 66 | 273 | 683.9 | 271 | -25.2312 | 59.1092
2005-02-05 | 9:59 | 20 | 14.4 | -33.3 | 67 | 272 | 684 | 258 | -25.2375 | 56.2717
2005-02-05 | 10:59 | 17 | 12.8 | -33.1 | 66 | 254 | 684.1 | 260 | -24.975 | 56.792
2005-02-05 | 11:59 | 14 | 12 | -32.8 | 67 | 261 | 684.3 | 238 | -25.3625 | 51.8729
2005-02-05 | 12:59 | 22 | 10 | -33.2 | 67 | 286 | 684.4 | 248 | -25.45 | 54.0257
2005-02-05 | 13:59 | 34 | 9.7 | -33.3 | 69 | 289 | 684.4 | 269 | -24.8938 | 58.7848
2005-02-05 | 14:59 | 34 | 11.2 | -33.7 | 67 | 292 | 684.6 | 279 | -24.9812 | 60.94
2005-02-05 | 15:59 | 46 | 9.6 | -33.6 | 66 | 274 | 684.6 | 250 | -25.7875 | 54.3575
2005-02-05 | 16:59 | 37 | 10.8 | -33.1 | 67 | 245 | 684.5 | 238 | -25.6625 | 51.7849
2005-02-05 | 17:59 | 55 | 7.6 | -33.1 | 68 | 227 | 684.6 | 233 | -25.8188 | 50.6522
2005-02-05 | 18:59 | 50 | 8.2 | -33.6 | 70 | 216 | 684.6 | 244 | -25.975 | 52.9965
2005-02-05 | 19:59 | 65 | 7.9 | -33.5 | 70 | 222 | 684.5 | 234 | -26.1875 | 50.7633
2005-02-05 | 20:59 | 66 | 8.2 | -33.6 | 70 | 245 | 684.5 | 224 | -26.6 | 48.4801
2005-02-05 | 21:59 | 71 | 8 | -34 | 69 | 233 | 684.4 | 242 | -26.4375 | 52.4242
2005-02-05 | 22:59 | 59 | 9.8 | -33.9 | 69 | 275 | 684.4 | 236 | -26.525 | 51.099
2005-02-05 | 23:59 | 71 | 8.6 | -35.2 | 67 | 277 | 684.4 | 285 | -26.2937 | 61.7897
2005-02-06 | 0:59 | 76 | 7.6 | -36.1 | 66 | 306 | 684.3 | 286 | -27.1625 | 61.7004
2005-02-06 | 1:59 | 64 | 8.9 | -35.3 | 67 | 296 | 684.3 | 283 | -26.4563 | 61.2995
2005-02-06 | 2:59 | 60 | 9.1 | -35.6 | 66 | 270 | 684.1 | 268 | -27.225 | 57.7966
2005-02-06 | 3:59 | 42 | 6 | -36.9 | 65 | 303 | 684.1 | 283 | -28.0562 | 60.7416
2005-02-06 | 4:59 | 64 | 7.3 | -36.2 | 65 | 320 | 684 | 318 | -26.2625 | 68.9566
2005-02-06 | 5:59 | 52 | 7.9 | -36.5 | 63 | 166 | 684.1 | 266 | -28.1875 | 57.0498
2005-02-06 | 6:59 | 54 | 7.8 | -36.5 | 61 | 312 | 684.2 | 295 | -27.2812 | 63.5989
2005-02-06 | 7:59 | 62 | 8.4 | -37 | 61 | 324 | 684.3 | 296 | -27.75 | 63.6436
2005-02-06 | 8:59 | 62 | 9.7 | -36.6 | 61 | 318 | 684.3 | 323 | -26.5063 | 69.9438
2005-02-06 | 9:59 | 51 | 11.8 | -36.8 | 61 | 299 | 684.4 | 309 | -27.1438 | 66.6695
2005-02-06 | 10:59 | 51 | 11.3 | -36.7 | 61 | 309 | 684.4 | 295 | -27.4812 | 63.5262
2005-02-06 | 11:59 | 45 | 11 | -36.8 | 60 | 255 | 684.5 | 285 | -27.8938 | 61.2279
2005-02-06 | 12:59 | 41 | 12 | -36.7 | 61 | 292 | 684.5 | 274 | -28.1375 | 58.7825
2005-02-06 | 13:59 | 52 | 8.3 | -37.2 | 60 | 283 | 684.8 | 280 | -28.45 | 59.9619
2005-02-06 | 14:59 | 86 | 3.1 | -37.6 | 61 | 269 | 685 | 277 | -28.9438 | 59.1509
2005-02-06 | 15:59 | 60 | 8.9 | -37.4 | 62 | 274 | 684.9 | 275 | -28.8062 | 58.7704
2005-02-06 | 16:59 | 55 | 9.7 | -37.4 | 62 | 278 | 684.9 | 279 | -28.6812 | 59.6683
2005-02-06 | 17:59 | 70 | 8.1 | -38.2 | 62 | 274 | 685.3 | 275 | -29.6062 | 58.4994
2005-02-06 | 18:59 | 72 | 7.7 | -37.9 | 62 | 277 | 685.6 | 275 | -29.3062 | 58.601
2005-02-06 | 19:59 | 57 | 8.1 | -37.9 | 62 | 276 | 685.7 | 277 | -29.2437 | 59.0486
2005-02-06 | 20:59 | 56 | 10.1 | -38.1 | 62 | 278 | 685.7 | 271 | -29.6313 | 57.6402
2005-02-06 | 21:59 | 44 | 9.5 | -37.4 | 63 | 244 | 686.1 | 278 | -28.7125 | 59.4437
2005-02-06 | 22:59 | 41 | 9.2 | -37.3 | 63 | 286 | 686.4 | 283 | -28.4563 | 60.6022
2005-02-06 | 23:59 | 50 | 11.5 | -37.8 | 62 | 291 | 686.6 | 289 | -28.7688 | 61.7757
2005-02-07 | 0:59 | 43 | 9.5 | -37.7 | 62 | 297 | 686.8 | 293 | -28.5437 | 62.712
2005-02-07 | 1:59 | 49 | 10.1 | -37.7 | 62 | 302 | 686.9 | 299 | -28.3562 | 64.0653
2005-02-07 | 2:59 | 37 | 13 | -37.4 | 63 | 293 | 686.9 | 303 | -27.9312 | 65.081
2005-02-07 | 3:59 | 38 | 12.2 | -37 | 63 | 350 | 687.2 | 286 | -28.0625 | 61.3833
2005-02-07 | 4:59 | 29 | 10.6 | -37.1 | 62 | 310 | 687.5 | 312 | -27.35 | 67.2375
2005-02-07 | 5:59 | 39 | 7.9 | -36.9 | 63 | 203 | 687.8 | 243 | -29.3062 | 51.782
2005-02-07 | 6:59 | 42 | 8.2 | -37.4 | 61 | 303 | 688.1 | 276 | -28.775 | 58.9948
2005-02-07 | 7:59 | 50 | 7.5 | -38.5 | 60 | 304 | 688.3 | 306 | -28.9375 | 65.346
2005-02-07 | 8:59 | 63 | 6 | -38.6 | 61 | 292 | 688.5 | 289 | -29.5688 | 61.4909
2005-02-07 | 9:59 | 63 | 7.2 | -39.6 | 60 | 294 | 688.6 | 300 | -30.225 | 63.5888
2005-02-07 | 10:59 | 56 | 9 | -39.4 | 60 | 292 | 688.6 | 293 | -30.2437 | 62.0983
2005-02-07 | 11:59 | 59 | 6.7 | -39.5 | 60 | 287 | 688.7 | 282 | -30.6875 | 59.6128
2005-02-07 | 12:59 | 55 | 7.1 | -39.6 | 60 | 273 | 688.7 | 284 | -30.725 | 60.0225
2005-02-07 | 13:59 | 63 | 8.2 | -38.9 | 60 | 277 | 688.6 | 276 | -30.275 | 58.4847
2005-02-07 | 14:59 | 67 | 8.9 | -39 | 60 | 266 | 688.6 | 273 | -30.4688 | 57.7839
2005-02-07 | 15:59 | 60 | 7.5 | -38.7 | 60 | 251 | 688.5 | 254 | -30.7625 | 53.6704
2005-02-07 | 16:59 | 70 | 6.4 | -39.7 | 59 | 238 | 688.3 | 261 | -31.5437 | 54.8982
2005-02-07 | 17:59 | 102 | 4.9 | -40.4 | 59 | 270 | 688.3 | 266 | -32.0875 | 55.7717
2005-02-07 | 18:59 | 83 | 6.6 | -40.9 | 59 | 272 | 688.2 | 270 | -32.4625 | 56.4857
2005-02-07 | 19:59 | 86 | 7.9 | -41 | 59 | 271 | 688.2 | 272 | -32.5 | 56.8915
2005-02-07 | 20:59 | 83 | 8.4 | -41 | 59 | 272 | 687.9 | 267 | -32.6562 | 55.7943
2005-02-07 | 21:59 | 77 | 9.6 | -40.8 | 59 | 276 | 687.7 | 274 | -32.2375 | 57.3985
2005-02-07 | 22:59 | 70 | 9.8 | -40.5 | 59 | 281 | 687.7 | 279 | -31.7812 | 58.6027
2005-02-07 | 23:59 | 84 | 7.9 | -40.7 | 59 | 286 | 687.5 | 283 | -31.8562 | 59.4167
2005-02-08 | 0:59 | 77 | 10.4 | -40.5 | 59 | 291 | 687 | 289 | -31.4688 | 60.8144
2005-02-08 | 1:59 | 83 | 11.8 | -40.3 | 59 | 296 | 686.7 | 294 | -31.1125 | 61.9956
2005-02-08 | 2:59 | 69 | 10.5 | -40.4 | 59 | 301 | 686.4 | 299 | -31.0562 | 63.0707
2005-02-08 | 3:59 | 73 | 9.4 | -40.4 | 59 | 305 | 686.1 | 301 | -30.9937 | 63.5157
2005-02-08 | 4:59 | 69 | 10.1 | -40 | 60 | 307 | 685.8 | 306 | -30.4375 | 64.7805
2005-02-08 | 5:59 | 76 | 10.4 | -39.7 | 60 | 159 | 685.6 | 253 | -31.7937 | 53.1376
2005-02-08 | 6:59 | 77 | 8 | -40.2 | 59 | 309 | 685.7 | 278 | -31.5125 | 58.4847
2005-02-08 | 7:59 | 75 | 5.8 | -40.8 | 59 | 307 | 685.6 | 308 | -31.175 | 64.9241
2005-02-08 | 8:59 | 83 | 8.3 | -41.2 | 58 | 305 | 685.4 | 304 | -31.7 | 63.8843
2005-02-08 | 9:59 | 75 | 9.5 | -41.5 | 58 | 301 | 685.1 | 303 | -32.0312 | 63.5505
2005-02-08 | 10:59 | 76 | 7.7 | -41.8 | 58 | 295 | 685 | 298 | -32.4875 | 62.3343
2005-02-08 | 11:59 | 80 | 7.8 | -42 | 58 | 294 | 684.9 | 294 | -32.8125 | 61.3798
2005-02-08 | 12:59 | 78 | 7.3 | -42.1 | 58 | 282 | 684.7 | 288 | -33.1 | 60.0252
2005-02-08 | 13:59 | 71 | 8.8 | -42.3 | 58 | 264 | 684.4 | 279 | -33.5812 | 57.984
2005-02-08 | 14:59 | 72 | 8 | -42.3 | 59 | 238 | 684.3 | 238 | -34.8625 | 49.0874
2005-02-08 | 15:59 | 70 | 7.3 | -42.2 | 59 | 229 | 684.3 | 255 | -34.2313 | 52.7919
2005-02-08 | 16:59 | 67 | 8.4 | -42.4 | 59 | 257 | 684.3 | 244 | -34.775 | 50.3512
2005-02-08 | 17:59 | 60 | 8.5 | -42.1 | 59 | 261 | 684.4 | 252 | -34.225 | 52.1728
2005-02-08 | 18:59 | 57 | 6.8 | -41.7 | 60 | 270 | 684.4 | 271 | -33.2313 | 56.4382
2005-02-08 | 19:59 | 57 | 7.4 | -42.3 | 59 | 221 | 684.4 | 249 | -34.5187 | 51.4616
2005-02-08 | 20:59 | 44 | 5.5 | -42.9 | 59 | 214 | 684.6 | 235 | -35.5562 | 48.2678
2005-02-08 | 21:59 | 56 | 6.5 | -43 | 59 | 235 | 684.6 | 221 | -36.0938 | 45.2459
2005-02-08 | 22:59 | 52 | 3.2 | -42.7 | 59 | 221 | 684.9 | 267 | -34.3563 | 55.2351
2005-02-08 | 23:59 | 58 | 3.3 | -42.4 | 59 | 266 | 684.9 | 275 | -33.8062 | 57.0764
2005-02-09 | 0:59 | 40 | 3 | -43.1 | 58 | 275 | 685.1 | 267 | -34.7563 | 55.1035
2005-02-09 | 1:59 | 51 | 4.1 | -43.7 | 57 | 261 | 685 | 263 | -35.4813 | 54.0431
2005-02-09 | 2:59 | 26 | 2.8 | -43.8 | 58 | 297 | 685.1 | 246 | -36.1125 | 50.3585
2005-02-09 | 3:59 | 19 | 2.8 | -44 | 58 | 297 | 685.3 | 271 | -35.5312 | 55.6703
2005-02-09 | 4:59 | 14 | 4.6 | -42.4 | 59 | 328 | 685.3 | 310 | -32.7125 | 64.7584
2005-02-09 | 5:59 | 22 | 2 | -41.7 | 60 | 165 | 685.6 | 263 | -33.4813 | 54.6911
2005-02-09 | 6:59 | 333 | 2.9 | -42 | 60 | 311 | 685.8 | 269 | -33.5938 | 55.9016
2005-02-09 | 7:59 | 33 | 1.9 | -42.9 | 59 | 297 | 686 | 287 | -33.9312 | 59.5229
2005-02-09 | 8:59 | 326 | 2.8 | -42.8 | 59 | 201 | 686.2 | 258 | -34.7375 | 53.2521
2005-02-09 | 9:59 | 354 | 1.9 | -42.8 | 59 | 246 | 686.3 | 239 | -35.3312 | 49.1556
2005-02-09 | 10:59 | 81 | 0 | -43.2 | 58 | 249 | 686.3 | 238 | -35.7625 | 48.8235
2005-02-09 | 11:59 | 0 | 2.2 | -43 | 58 | 252 | 686.5 | 228 | -35.875 | 46.7405
2005-02-09 | 12:59 | 354 | 5.5 | -43 | 57 | 285 | 686.5 | 271 | -34.5312 | 56.0042
2005-02-09 | 13:59 | 335 | 3.1 | -43.4 | 57 | 288 | 686.6 | 286 | -34.4625 | 59.1283
2005-02-09 | 14:59 | 328 | 1.3 | -43.3 | 58 | 245 | 686.6 | 269 | -34.8937 | 55.4707
2005-02-09 | 15:59 | 30 | 0 | -43.3 | 58 | 212 | 686.6 | 233 | -36.0187 | 47.7242
2005-02-09 | 16:59 | 345 | 0 | -44.1 | 58 | 245 | 686.7 | 184 | -38.35 | 37.1593
2005-02-09 | 17:59 | 352 | 2.7 | -43.2 | 59 | 239 | 686.7 | 269 | -34.7938 | 55.5039
2005-02-09 | 18:59 | 66 | 2.4 | -43.4 | 59 | 196 | 686.7 | 201 | -37.1187 | 40.8974
2005-02-09 | 19:59 | 3 | 4.6 | -44.1 | 58 | 230 | 686.8 | 214 | -37.4125 | 43.4651
2005-02-09 | 20:59 | 15 | 3.8 | -43 | 59 | 206 | 686.8 | 224 | -36 | 45.886
2005-02-09 | 21:59 | 18 | 4.2 | -43.3 | 58 | 242 | 686.7 | 264 | -35.05 | 54.3889
2005-02-09 | 22:59 | 353 | 6.5 | -43.4 | 58 | 190 | 686.8 | 240 | -35.9 | 49.1931
2005-02-09 | 23:59 | 10 | 5.5 | -43.1 | 58 | 290 | 686.6 | 244 | -35.475 | 50.1407
2005-02-10 | 0:59 | 7 | 7.4 | -44.1 | 58 | 206 | 686.5 | 226 | -37.0375 | 46.0068
2005-02-10 | 1:59 | 7 | 9.1 | -42.7 | 59 | 222 | 686.2 | 254 | -34.7625 | 52.4186
2005-02-10 | 2:59 | 4 | 8.8 | -42.6 | 59 | 283 | 686 | 268 | -34.225 | 55.4853
2005-02-10 | 3:59 | 18 | 8.2 | -42.9 | 60 | 290 | 685.8 | 283 | -34.0562 | 58.6497
2005-02-10 | 4:59 | 14 | 10.1 | -42.3 | 60 | 296 | 685.7 | 277 | -33.6437 | 57.547
2005-02-10 | 5:59 | 19 | 10.2 | -41.8 | 61 | 85 | 685.6 | 241 | -34.2687 | 49.8824
2005-02-10 | 6:59 | 25 | 7.5 | -42.7 | 59 | 295 | 685.7 | 263 | -34.4813 | 54.3671
2005-02-10 | 7:59 | 16 | 5.1 | -43.2 | 59 | 289 | 685.7 | 290 | -34.1375 | 60.0714
2005-02-10 | 8:59 | 27 | 8.5 | -43.3 | 59 | 288 | 685.5 | 282 | -34.4875 | 58.2926
2005-02-10 | 9:59 | 19 | 11.5 | -42.7 | 60 | 284 | 685.3 | 285 | -33.7938 | 59.1563
2005-02-10 | 10:59 | 22 | 12.1 | -42.5 | 60 | 279 | 685 | 281 | -33.7188 | 58.352
2005-02-10 | 11:59 | 16 | 12.1 | -42.3 | 59 | 272 | 684.8 | 276 | -33.675 | 57.3286
2005-02-10 | 12:59 | 15 | 14.5 | -42.3 | 59 | 266 | 684.7 | 269 | -33.8937 | 55.8021
2005-02-10 | 13:59 | 18 | 12.6 | -42.3 | 59 | 261 | 684.6 | 263 | -34.0812 | 54.4967
2005-02-10 | 14:59 | 28 | 12.5 | -42.5 | 58 | 267 | 684.4 | 260 | -34.375 | 53.781
2005-02-10 | 15:59 | 23 | 11.9 | -42.6 | 58 | 255 | 684.2 | 257 | -34.5688 | 53.0991
2005-02-10 | 16:59 | 17 | 12.5 | -42.5 | 58 | 250 | 683.9 | 252 | -34.625 | 52.0486
2005-02-10 | 17:59 | 19 | 13.4 | -41.7 | 59 | 230 | 683.8 | 250 | -33.8875 | 51.8627
2005-02-10 | 18:59 | 24 | 15 | -42.8 | 59 | 284 | 683.5 | 155 | -37.9562 | 31.3779
2005-02-10 | 19:59 | 16 | 15 | -41.6 | 59 | 216 | 682.9 | 265 | -33.3188 | 55.1601
2005-02-10 | 20:59 | 21 | 11.6 | -41.5 | 59 | 160 | 683.2 | 181 | -35.8438 | 37.1123
2005-02-10 | 21:59 | 9 | 18.5 | -40.3 | 60 | 240 | 682.7 | 225 | -33.2687 | 46.8479
2005-02-10 | 22:59 | 12 | 16.3 | -40.4 | 61 | 162 | 682.6 | 188 | -34.525 | 38.8531
2005-02-10 | 23:59 | 10 | 18.4 | -40.2 | 61 | 158 | 682.5 | 168 | -34.95 | 34.6318
2005-02-11 | 0:59 | 7 | 18.3 | -39.5 | 62 | 169 | 682.3 | 166 | -34.3125 | 34.3499
2005-02-11 | 1:59 | 6 | 18.8 | -39.1 | 62 | 189 | 682.3 | 190 | -33.1625 | 39.5853
2005-02-11 | 2:59 | 10 | 17.6 | -38.6 | 62 | 205 | 682 | 180 | -32.975 | 37.5435
2005-02-11 | 3:59 | 9 | 16.9 | -38.2 | 62 | 200 | 681.9 | 200 | -31.95 | 41.9675
2005-02-11 | 4:59 | 15 | 18.1 | -37.8 | 63 | 202 | 681.8 | 188 | -31.925 | 39.4553
2005-02-11 | 5:59 | 12 | 16.2 | -37.8 | 62 | 219 | 681.8 | 215 | -31.0813 | 45.3452
2005-02-11 | 6:59 | 12 | 20.4 | -37.5 | 63 | 131 | 681.7 | 186 | -31.6875 | 39.0899
2005-02-11 | 7:59 | 14 | 18.7 | -36.6 | 64 | 244 | 681.5 | 159 | -31.6313 | 33.4266
2005-02-11 | 8:59 | 16 | 16.1 | -36.9 | 63 | 243 | 681.8 | 214 | -30.2125 | 45.3633
2005-02-11 | 9:59 | 20 | 18.7 | -36.8 | 63 | 182 | 681.8 | 215 | -30.0813 | 45.6101
2005-02-11 | 10:59 | 15 | 19.8 | -36.4 | 64 | 188 | 681.8 | 178 | -30.8375 | 37.5951
2005-02-11 | 11:59 | 10 | 17.2 | -37.2 | 63 | 217 | 681.8 | 192 | -31.2 | 40.4662
2005-02-11 | 12:59 | 22 | 18.1 | -36.8 | 63 | 190 | 681.8 | 242 | -29.2375 | 51.5894
2005-02-11 | 13:59 | 15 | 19.9 | -36.7 | 63 | 250 | 681.6 | 231 | -29.4812 | 49.1751
2005-02-11 | 14:59 | 14 | 15.8 | -37.1 | 63 | 193 | 681.6 | 214 | -30.4125 | 45.3106
2005-02-11 | 15:59 | 19 | 19.6 | -36.2 | 64 | 190 | 681.6 | 189 | -30.2937 | 40.045
2005-02-11 | 16:59 | 10 | 22.7 | -35.9 | 64 | 237 | 681.5 | 209 | -29.3687 | 44.5207
2005-02-11 | 17:59 | 9 | 19.4 | -36.7 | 64 | 138 | 681.7 | 195 | -30.6062 | 41.2412
2005-02-11 | 18:59 | [6 empty] | 190 | 5.9375 | 48.7379
2005-02-11 | 21:59 | 14 | 22.6 | -36.3 | 64 | 186 | 682.3 | 189 | -30.3938 | 40.0217
2005-02-11 | 22:59 | 23 | 17.9 | -36 | 65 | 200 | 682.3 | 187 | -30.1562 | 39.6529
2005-02-11 | 23:59 | 29 | 18.2 | -37.5 | 63 | 265 | 682.5 | 218 | -30.6875 | 46.0837
2005-02-12 | 0:59 | 27 | 20.3 | -37 | 63 | 175 | 682.5 | 220 | -30.125 | 46.6589
2005-02-12 | 1:59 | 21 | 19.5 | -36.6 | 64 | 155 | 682.3 | 133 | -32.4438 | 27.8275
2005-02-12 | 2:59 | 15 | 20.4 | -34.9 | 66 | 124 | 682.2 | 155 | -30.0562 | 32.8865
2005-02-12 | 3:59 | 15 | 24.3 | -33.7 | 67 | 151 | 682 | 145 | -29.1687 | 30.9233
2005-02-12 | 4:59 | 12 | 21 | -33.8 | 67 | 172 | 682.1 | 152 | -29.05 | 32.4384
2005-02-12 | 5:59 | 10 | 23.7 | -33.6 | 67 | 156 | 682.2 | 166 | -28.4125 | 35.5565
2005-02-12 | 6:59 | 10 | 22.2 | -32.8 | 68 | 135 | 682.3 | 152 | -28.05 | 32.6256
2005-02-12 | 7:59 | 13 | 23 | -32.3 | 68 | 225 | 682.4 | 178 | -26.7375 | 38.4942
2005-02-12 | 8:59 | 18 | 21.1 | -32.2 | 68 | 114 | 682.8 | 133 | -28.0437 | 28.5485
2005-02-12 | 9:59 | 15 | 25.5 | -32 | 69 | 165 | 682.9 | 143 | -27.5312 | 30.7853
2005-02-12 | 10:59 | 9 | 21.4 | -31.1 | 69 | 147 | 682.9 | 153 | -26.3188 | 33.1666
2005-02-12 | 11:59 | 13 | 23.7 | -30.5 | 70 | 129 | 683 | 139 | -26.1562 | 30.1596
2005-02-12 | 12:59 | 15 | 20.7 | -30.1 | 70 | 161 | 683.3 | 140 | -25.725 | 30.451
2005-02-12 | 13:59 | 10 | 17.9 | -30.3 | 70 | 139 | 683.4 | 173 | -24.8938 | 37.8058
2005-02-12 | 14:59 | 10 | 18.8 | -29.4 | 71 | 172 | 683.6 | 150 | -24.7125 | 32.8131
2005-02-12 | 15:59 | 9 | 19.9 | -29.2 | 70 | 189 | 683.4 | 183 | -23.4812 | 40.3096
2005-02-12 | 16:59 | 9 | 22.4 | -29.6 | 70 | 126 | 683.3 | 171 | -24.2563 | 37.5031
2005-02-12 | 17:59 | 12 | 20.6 | -29.1 | 71 | 187 | 683.8 | 162 | -24.0375 | 35.5729
2005-02-12 | 18:59 | 4 | 24.3 | -29.1 | 70 | 235 | 684.2 | 206 | -22.6625 | 45.5836
2005-02-12 | 19:59 | 14 | 19.6 | -28.6 | 69 | 242 | 684.6 | 285 | -19.6938 | 64.1071
2005-02-12 | 20:59 | 9 | 21.5 | -28.7 | 69 | 229 | 684.6 | 255 | -20.7312 | 57.0331
2005-02-12 | 21:59 | 16 | 17.5 | -29.7 | 69 | 143 | 684.9 | 194 | -23.6375 | 42.6952
2005-02-12 | 22:59 | 31 | 14.4 | -30.2 | 69 | 183 | 685.1 | 145 | -25.6687 | 31.5485
2005-02-12 | 23:59 | 16 | 16 | -30.1 | 69 | 127 | 685.1 | 182 | -24.4125 | 39.8805
2005-02-13 | 0:59 | 17 | 18.8 | -30.1 | 69 | 223 | 684.9 | 162 | -25.0375 | 35.3733
2005-02-13 | 1:59 | 26 | 16.9 | -30.6 | 69 | 165 | 685 | 198 | -24.4125 | 43.3865
2005-02-13 | 2:59 | 28 | 15.7 | -30.8 | 69 | 192 | 684.8 | 176 | -25.3 | 38.3734
2005-02-13 | 3:59 | 25 | 15.8 | -30.7 | 68 | 314 | 684.5 | 253 | -22.7937 | 55.9429
2005-02-13 | 4:59 | 21 | 17.9 | -30.6 | 68 | 145 | 684.5 | 282 | -21.7875 | 62.7049
2005-02-13 | 5:59 | 29 | 19.1 | -30.9 | 68 | 194 | 684.6 | 185 | -25.1187 | 40.3769
2005-02-13 | 6:59 | 30 | 18.2 | -32.6 | 67 | 169 | 684.6 | 176 | -27.1 | 37.9831
2005-02-13 | 7:59 | 29 | 13.8 | -32.7 | 66 | 246 | 684.7 | 206 | -26.2625 | 44.67
2005-02-13 | 8:59 | 33 | 15.6 | -33.6 | 64 | 217 | 684.3 | 272 | -25.1 | 59.3713
2005-02-13 | 9:59 | 30 | 16.8 | -32.6 | 64 | 339 | 684.1 | 270 | -24.1625 | 59.2466
2005-02-13 | 10:59 | 35 | 19.1 | -33.2 | 63 | 261 | 683.9 | 286 | -24.2625 | 62.7223
2005-02-13 | 11:59 | 33 | 16.6 | -33.6 | 63 | 254 | 683.5 | 257 | -25.5688 | 55.9487
2005-02-13 | 12:59 | 33 | 19.8 | -33.3 | 63 | 248 | 683.3 | 251 | -25.4563 | 54.6773
2005-02-13 | 13:59 | 35 | 16 | -33.4 | 62 | 243 | 683 | 245 | -25.7437 | 53.2835
2005-02-13 | 14:59 | 37 | 18.8 | -33.5 | 62 | 236 | 682.6 | 240 | -26 | 52.1203
2005-02-13 | 15:59 | 47 | 17 | -33.6 | 62 | 234 | 682.3 | 236 | -26.225 | 51.1862
2005-02-13 | 16:59 | 42 | 14.5 | -33.9 | 61 | 232 | 681.8 | 233 | -26.6187 | 50.4225
2005-02-13 | 17:59 | 51 | 14.8 | -33.9 | 61 | 236 | 681.3 | 233 | -26.6187 | 50.4225
2005-02-13 | 18:59 | 48 | 16.1 | -34.3 | 60 | 226 | 681 | 236 | -26.925 | 50.9827
2005-02-13 | 19:59 | 53 | 17 | -34.7 | 59 | 226 | 680.5 | 213 | -28.0437 | 45.7205
2005-02-13 | 20:59 | 55 | 20.2 | -34.4 | 59 | 230 | 679.8 | 224 | -27.4 | 48.2593
2005-02-13 | 21:59 | 62 | 16.6 | -34.4 | 59 | 245 | 679.2 | 242 | -26.8375 | 52.305
2005-02-13 | 22:59 | 69 | 18 | -34.8 | 59 | 220 | 678.3 | 239 | -27.3313 | 51.5112
2005-02-13 | 23:59 | 71 | 17.2 | -34.9 | 59 | 247 | 677.4 | 239 | -27.4312 | 51.4817
2005-02-14 | 0:59 | 72 | 16 | -35.5 | 59 | 253 | 676.7 | 250 | -27.6875 | 53.7722
2005-02-14 | 1:59 | 71 | 18.1 | -36.3 | 60 | 258 | 676 | 255 | -28.3313 | 54.6455
2005-02-14 | 2:59 | 55 | 18 | -36.7 | 60 | 262 | 675.3 | 261 | -28.5437 | 55.8629
2005-02-14 | 3:59 | 59 | 15.2 | -36.9 | 60 | 266 | 674.6 | 263 | -28.6812 | 56.2464
2005-02-14 | 4:59 | 52 | 17.1 | -36.9 | 61 | 256 | 674.1 | 264 | -28.65 | 56.4704
2005-02-14 | 5:59 | 49 | 19.4 | -36.8 | 63 | 194 | 673.7 | 197 | -30.6438 | 41.655
2005-02-14 | 6:59 | 45 | 21.1 | -36.7 | 64 | 210 | 673.3 | 175 | -31.2312 | 36.8765
2005-02-14 | 7:59 | 40 | 18.6 | -36.3 | 65 | 182 | 672.9 | 175 | -30.8313 | 36.9628
2005-02-14 | 8:59 | 32 | 26.2 | -35.7 | 66 | 161 | 672.3 | 170 | -30.3875 | 35.9996
2005-02-14 | 9:59 | 26 | 23.7 | -34.8 | 67 | 122 | 672.5 | 150 | -30.1125 | 31.8152
2005-02-14 | 10:59 | 27 | 18.1 | -33.5 | 68 | 134 | 672.6 | 131 | -29.4062 | 27.8993
2005-02-14 | 11:59 | 23 | 27.7 | -33.7 | 68 | 142 | 672.5 | 141 | -29.2937 | 30.0485
2005-02-14 | 12:59 | 20 | 27.1 | -34.1 | 68 | 141 | 672.6 | 141 | -29.6938 | 29.979
2005-02-14 | 13:59 | 15 | 26.8 | -33.9 | 68 | 138 | 672.9 | 142 | -29.4625 | 30.2321
2005-02-14 | 14:59 | 9 | 25 | -34.2 | 68 | 133 | 673.1 | 141 | -29.7937 | 29.9617
2005-02-14 | 15:59 | 9 | 31.1 | -34.4 | 67 | 159 | 673.3 | 163 | -29.3062 | 34.7344
2005-02-14 | 16:59 | 17 | 26.3 | -34.8 | 67 | 146 | 673.7 | 162 | -29.7375 | 34.4353
2005-02-14 | 17:59 | 16 | 22.4 | -34.9 | 67 | 128 | 674.2 | 136 | -30.65 | 28.7557
2005-02-14 | 18:59 | 12 | 21.9 | -34.5 | 67 | 168 | 674.7 | 189 | -28.5938 | 40.4408
2005-02-14 | 19:59 | 6 | 19.8 | -34.3 | 67 | 180 | 675 | 180 | -28.675 | 38.497
2005-02-14 | 20:59 | 16 | 20.4 | -34.4 | 66 | 181 | 675.2 | 194 | -28.3375 | 41.5719
2005-02-14 | 21:59 | 12 | 20.1 | -34.9 | 66 | 170 | 675.5 | 163 | -29.8062 | 34.634
2005-02-14 | 22:59 | 9 | 17.2 | -34.9 | 66 | 176 | 675.7 | 150 | -30.2125 | 31.7967
2005-02-14 | 23:59 | 4 | 16.2 | -35.1 | 66 | 155 | 676 | 161 | -30.0688 | 34.157
2005-02-15 | 0:59 | 4 | 17.3 | -35.2 | 66 | 147 | 676.4 | 165 | -30.0437 | 35.0107
2005-02-15 | 1:59 | 5 | 16.9 | -35.3 | 65 | 223 | 676.6 | 194 | -29.2375 | 41.3568
2005-02-15 | 2:59 | 10 | 14.4 | -35.7 | 65 | 230 | 676.7 | 224 | -28.7 | 47.9005
2005-02-15 | 3:59 | 4 | 14.8 | -34.3 | 67 | 121 | 677.1 | 161 | -29.2688 | 34.3157
2005-02-15 | 4:59 | 5 | 15.4 | -33.4 | 67 | 135 | 677.4 | 137 | -29.1187 | 29.2256
2005-02-15 | 5:59 | 8 | 15.7 | -33.2 | 67 | 138 | 677.6 | 144 | -28.7 | 30.7932
2005-02-15 | 6:59 | 10 | 17 | -33.6 | 67 | 162 | 677.9 | 158 | -28.6625 | 33.7943
2005-02-15 | 7:59 | 17 | 12.6 | -34 | 67 | 148 | 677.9 | 162 | -28.9375 | 34.5949
2005-02-15 | 8:59 | 23 | 11.8 | -34.8 | 66 | 152 | 678.1 | 148 | -30.175 | 31.3796
2005-02-15 | 9:59 | 21 | 11 | -34.7 | 66 | 253 | 678.2 | 204 | -28.325 | 43.7179
2005-02-15 | 10:59 | 33 | 8.7 | -35.5 | 66 | 228 | 678.2 | 231 | -28.2812 | 49.5166
2005-02-15 | 11:59 | 49 | 8.8 | -36 | 65 | 172 | 678.3 | 195 | -29.9062 | 41.4093
2005-02-15 | 12:59 | 58 | 9.1 | -36.5 | 64 | 199 | 678 | 209 | -29.9688 | 44.3662
2005-02-15 | 13:59 | 53 | 8.8 | -36.4 | 63 | 232 | 678 | 227 | -29.3062 | 48.3725
2005-02-15 | 14:59 | 50 | 11.9 | -36.4 | 63 | 226 | 677.8 | 228 | -29.275 | 48.5944
2005-02-15 | 15:59 | 65 | 9.1 | -37 | 63 | 221 | 677.7 | 223 | -30.0312 | 47.3209
2005-02-15 | 16:59 | 64 | 9.3 | -37.3 | 63 | 213 | 677.5 | 217 | -30.5188 | 45.9174
2005-02-15 | 17:59 | 56 | 9.4 | -37.2 | 64 | 217 | 677.3 | 215 | -30.4812 | 45.5041
2005-02-15 | 18:59 | 47 | 15.5 | -36.3 | 64 | 216 | 677.3 | 216 | -29.55 | 45.9636
2005-02-15 | 19:59 | 38 | 13.8 | -36 | 64 | 214 | 677 | 215 | -29.2812 | 45.822
2005-02-15 | 20:59 | 37 | 13.3 | -36.2 | 64 | 209 | 677 | 210 | -29.6375 | 44.6642
2005-02-15 | 21:59 | 38 | 14.8 | -36.2 | 64 | 215 | 677 | 213 | -29.5437 | 45.3268
2005-02-15 | 22:59 | 28 | 14.2 | -36.2 | 64 | 213 | 677 | 214 | -29.5125 | 45.5479
2005-02-15 | 23:59 | 27 | 14.1 | -36.3 | 64 | 218 | 677.1 | 216 | -29.55 | 45.9636
2005-02-16 | 0:59 | 30 | 14.4 | -36.7 | 63 | 222 | 677.1 | 222 | -29.7625 | 47.1822
2005-02-16 | 1:59 | 26 | 18.3 | -36.9 | 63 | 233 | 676.9 | 229 | -29.7437 | 48.6753
2005-02-16 | 2:59 | 18 | 15.7 | -37.2 | 63 | 234 | 677.1 | 232 | -29.95 | 49.254
2005-02-16 | 3:59 | 16 | 15.4 | -37.4 | 63 | 219 | 677 | 219 | -30.5562 | 46.3305
2005-02-16 | 4:59 | 34 | 19.5 | -37.1 | 63 | 191 | 677.2 | 200 | -30.85 | 42.2386
2005-02-16 | 5:59 | 32 | 14.6 | -37.1 | 63 | 186 | 677.3 | 168 | -31.85 | 35.2734
2005-02-16 | 6:59 | 27 | 16.5 | -37.2 | 63 | 236 | 677.1 | 209 | -30.6687 | 44.186
2005-02-16 | 7:59 | 38 | 15 | -37.3 | 63 | 245 | 677.1 | 235 | -29.9563 | 49.8891
2005-02-16 | 8:59 | 29 | 15.6 | -37.2 | 63 | 159 | 677 | 186 | -31.3875 | 39.1587
2005-02-16 | 9:59 | 40 | 15.4 | -37.5 | 62 | 228 | 676.8 | 222 | -30.5625 | 46.9634
2005-02-16 | 10:59 | 35 | 15.4 | -37.4 | 63 | 170 | 676.7 | 185 | -31.6187 | 38.8955
2005-02-16 | 11:59 | 48 | 17 | -36.9 | 64 | 170 | 676.3 | 148 | -32.275 | 30.9967
2005-02-16 | 12:59 | 35 | 14.1 | -37.3 | 63 | 207 | 676.2 | 188 | -31.425 | 39.5711
2005-02-16 | 13:59 | 33 | 16.8 | -37.7 | 63 | 122 | 675.9 | 194 | -31.6375 | 40.7832
2005-02-16 | 14:59 | 25 | 16.5 | -36.3 | 65 | 146 | 675.4 | 128 | -32.3 | 26.804
2005-02-16 | 15:59 | 36 | 15.8 | -36.6 | 64 | 192 | 675.2 | 196 | -30.475 | 41.4843
2005-02-16 | 16:59 | 30 | 16.9 | -37.4 | 63 | 145 | 675.1 | 159 | -32.4312 | 33.2699
2005-02-16 | 17:59 | 30 | 14.1 | -37.3 | 64 | 212 | 674.9 | 146 | -32.7375 | 30.4946
2005-02-16 | 18:59 | 43 | 13.6 | -37.2 | 64 | 188 | 674.7 | 187 | -31.3562 | 39.3764
2005-02-16 | 19:59 | 40 | 9.7 | -37.6 | 63 | 243 | 674.5 | 222 | -30.6625 | 46.9361
2005-02-16 | 20:59 | 48 | 9 | -38.4 | 62 | 217 | 674.2 | 232 | -31.15 | 48.911
2005-02-16 | 21:59 | 37 | 8.9 | -39.3 | 61 | 186 | 674 | 209 | -32.7687 | 43.6452
2005-02-16 | 22:59 | 45 | 9.7 | -39.3 | 62 | 218 | 673.6 | 204 | -32.925 | 42.5618
2005-02-16 | 23:59 | 62 | 9.1 | -40 | 61 | 225 | 673.4 | 222 | -33.0625 | 46.2797
2005-02-17 | 0:59 | 86 | 8 | -40.6 | 61 | 230 | 673.2 | 227 | -33.5063 | 47.1979
2005-02-17 | 1:59 | 87 | 7.7 | -40.7 | 61 | 234 | 672.9 | 231 | -33.4813 | 48.0367
2005-02-17 | 2:59 | 87 | 7.1 | -40.4 | 61 | 239 | 672.5 | 237 | -32.9937 | 49.4268
2005-02-17 | 3:59 | 80 | 7.9 | -40.8 | 61 | 243 | 672.1 | 240 | -33.3 | 49.9619
2005-02-17 | 4:59 | 72 | 10.7 | -40.2 | 61 | 250 | 671.8 | 245 | -32.5438 | 51.231
2005-02-17 | 5:59 | 80 | 7.6 | -40.6 | 61 | 244 | 671.5 | 187 | -34.7563 | 38.5931
2005-02-17 | 6:59 | 80 | 7.8 | -40.6 | 60 | 245 | 671.5 | 225 | -33.5688 | 46.7647
2005-02-17 | 7:59 | 80 | 7.3 | -40.7 | 60 | 234 | 671.3 | 239 | -33.2313 | 49.7739
2005-02-17 | 8:59 | 82 | 6.9 | -40.9 | 61 | 146 | 671.4 | 180 | -35.275 | 37.0334
2005-02-17 | 9:59 | 92 | 6.3 | -40 | 61 | 257 | 671.3 | 222 | -33.0625 | 46.2797
2005-02-17 | 10:59 | 67 | 6.7 | -40 | 62 | 142 | 671.3 | 190 | -34.0625 | 39.3747
2005-02-17 | 11:59 | 61 | 7.3 | -38.5 | 63 | 148 | 671.4 | 138 | -34.1875 | 28.5772
2005-02-17 | 12:59 | 50 | 9.3 | -38.3 | 63 | 136 | 671.4 | 138 | -33.9875 | 28.6112
2005-02-17 | 13:59 | 60 | 9.3 | -38 | 63 | 119 | 671.2 | 146 | -33.4375 | 30.3687
2005-02-17 | 14:59 | 43 | 10.9 | -36.2 | 64 | 131 | 671.2 | 129 | -32.1688 | 27.0343
2005-02-17 | 15:59 | 39 | 9.5 | -37.1 | 63 | 156 | 671.5 | 170 | -31.7875 | 35.7064
2005-02-17 | 16:59 | 35 | 11.2 | -37.4 | 62 | 176 | 671.7 | 197 | -31.2437 | 41.5094
2005-02-17 | 17:59 | 31 | 10.4 | -37.5 | 63 | 167 | 672 | 191 | -31.5312 | 40.1775
2005-02-17 | 18:59 | 32 | 11.2 | -38.1 | 62 | 212 | 672.2 | 185 | -32.3188 | 38.7359
2005-02-17 | 19:59 | 27 | 10.5 | -38.5 | 62 | 168 | 672.3 | 193 | -32.4688 | 40.3753
2005-02-17 | 20:59 | 29 | 11 | -38.8 | 62 | 143 | 672.7 | 161 | -33.7687 | 33.4231
2005-02-17 | 21:59 | 26 | 11.4 | -38.8 | 63 | 127 | 673.1 | 139 | -34.4562 | 28.7382
2005-02-17 | 22:59 | 20 | 10.7 | -39.4 | 62 | 181 | 673.5 | 160 | -34.4 | 33.0911
2005-02-17 | 23:59 | 50 | 7.7 | -40.1 | 61 | 137 | 673.7 | 175 | -34.6313 | 36.1435
2005-02-18 | 0:59 | 37 | 8.1 | -40.2 | 61 | 174 | 673.9 | 154 | -35.3875 | 31.6628
2005-02-18 | 1:59 | 43 | 7.6 | -39.6 | 61 | 153 | 674.3 | 219 | -32.7563 | 45.7369
2005-02-18 | 2:59 | 47 | 9.9 | -39.4 | 61 | 210 | 674.3 | 227 | -32.3062 | 47.5335
2005-02-18 | 3:59 | 31 | 10.2 | -40.3 | 61 | 207 | 674.4 | 173 | -34.8937 | 35.6745
2005-02-18 | 4:59 | 30 | 9.3 | -40.7 | 60 | 193 | 674.8 | 201 | -34.4188 | 41.566
2005-02-18 | 5:59 | 40 | 9.5 | -41.2 | 59 | 156 | 675 | 178 | -35.6375 | 36.5424
2005-02-18 | 6:59 | 36 | 11 | -41.9 | 59 | 87 | 675 | 105 | -38.6187 | 21.1703
2005-02-18 | 7:59 | 38 | 9 | -41.4 | 60 | 234 | 675.2 | 172 | -36.025 | 35.2286
2005-02-18 | 8:59 | 55 | 8.5 | -41.6 | 59 | 226 | 675.2 | 245 | -33.9438 | 50.8084
2005-02-18 | 9:59 | 55 | 7 | -42.3 | 58 | 165 | 675.4 | 165 | -37.1437 | 33.5674
2005-02-18 | 10:59 | 48 | 7 | -42 | 59 | 190 | 675.7 | 166 | -36.8125 | 33.8386
2005-02-18 | 11:59 | 58 | 6.3 | -42.8 | 58 | 220 | 675.9 | 194 | -36.7375 | 39.5642
2005-02-18 | 12:59 | 61 | 5.7 | -43.1 | 58 | 150 | 676 | 182 | -37.4125 | 36.9656
2005-02-18 | 13:59 | 67 | 4.9 | -43.9 | 58 | 177 | 676.1 | 166 | -38.7125 | 33.45
2005-02-18 | 14:59 | 72 | 4.3 | -44.6 | 57 | 127 | 676.1 | 159 | -39.6313 | 31.8595
2005-02-18 | 15:59 | 77 | 5.7 | -44.6 | 58 | 200 | 676.2 | 161 | -39.5688 | 32.2727
2005-02-18 | 16:59 | 53 | 4.4 | -44.2 | 58 | 251 | 676.3 | 209 | -37.6688 | 42.3835
2005-02-18 | 17:59 | 54 | 2.8 | -44.3 | 58 | 188 | 676.6 | 170 | -38.9875 | 34.1985
2005-02-18 | 18:59 | 80 | 2.4 | -44.3 | 58 | 134 | 676.6 | 169 | -39.0187 | 33.9908
2005-02-18 | 19:59 | 66 | 6 | -45.1 | 57 | 185 | 676.8 | 150 | -40.4125 | 29.9118
2005-02-18 | 20:59 | 54 | 6.5 | -44.9 | 57 | 170 | 676.7 | 186 | -39.0875 | 37.3942
2005-02-18 | 21:59 | 51 | 5.9 | -44.7 | 57 | 221 | 676.6 | 185 | -38.9188 | 37.2316
2005-02-18 | 22:59 | 63 | 4.7 | -44.3 | 58 | 182 | 676.7 | 215 | -37.5812 | 43.6235
2005-02-18 | 23:59 | 67 | 5.6 | -44.8 | 57 | 199 | 676.7 | 177 | -39.2687 | 35.5453
2005-02-19 | 0:59 | 69 | 7.7 | -44.6 | 57 | 165 | 676.4 | 198 | -38.4125 | 39.9714
2005-02-19 | 1:59 | 77 | 7.1 | -45 | 56 | 217 | 676 | 187 | -39.1562 | 37.5794
2005-02-19 | 2:59 | 85 | 7.4 | -45.2 | 56 | 223 | 675.9 | 211 | -38.6063 | 42.5454
2005-02-19 | 3:59 | 86 | 6.7 | -45.5 | 56 | 231 | 675.5 | 225 | -38.4688 | 45.4065
2005-02-19 | 4:59 | 113 | 6.6 | -45.1 | 56 | 235 | 675.4 | 232 | -37.85 | 46.996
2005-02-19 | 5:59 | 108 | 7.5 | -45.4 | 56 | 235 | 675.3 | 179 | -39.8062 | 35.8284
2005-02-19 | 6:59 | 113 | 8.7 | -45.2 | 56 | 234 | 675.1 | 214 | -38.5125 | 43.1751
2005-02-19 | 7:59 | 109 | 7.8 | -45.3 | 56 | 232 | 674.8 | 234 | -37.9875 | 47.3615
2005-02-19 | 8:59 | 121 | 11 | -45.1 | 57 | 230 | 674.5 | 230 | -37.9125 | 46.5731
2005-02-19 | 9:59 | 113 | 10.9 | -44.6 | 58 | 226 | 674.4 | 228 | -37.475 | 46.291
2005-02-19 | 10:59 | 121 | 8.1 | -44.3 | 58 | 222 | 674.3 | 224 | -37.3 | 45.5272
2005-02-19 | 11:59 | 116 | 7.4 | -44.7 | 58 | 215 | 674.2 | 218 | -37.8875 | 44.1499
2005-02-19 | 12:59 | 118 | 7.9 | -44.4 | 58 | 210 | 673.9 | 213 | -37.7437 | 43.175
2005-02-19 | 13:59 | 108 | 8.8 | -44.5 | 58 | 205 | 673.7 | 206 | -38.0625 | 41.6752
2005-02-19 | 14:59 | 116 | 8.5 | -44.4 | 59 | 200 | 673.5 | 202 | -38.0875 | 40.8598
2005-02-19 | 15:59 | 114 | 9 | -44.7 | 58 | 196 | 673.3 | 198 | -38.5125 | 39.947
2005-02-19 | 16:59 | 120 | 8.1 | -45.2 | 58 | 193 | 673.4 | 194 | -39.1375 | 38.9906
2005-02-19 | 17:59 | 110 | 6.6 | -45.2 | 58 | 194 | 673.4 | 192 | -39.2 | 38.5739
2005-02-19 | 18:59 | 118 | 7.7 | -45.3 | 58 | 194 | 673.6 | 192 | -39.3 | 38.5502
2005-02-19 | 19:59 | 119 | 9.2 | -45.4 | 58 | 193 | 673.4 | 193 | -39.3687 | 38.7347
2005-02-19 | 20:59 | 105 | 7.9 | -45.8 | 57 | 195 | 673.4 | 190 | -39.8625 | 38.017
2005-02-19 | 21:59 | 107 | 8.7 | -45.6 | 56 | 220 | 673.5 | 202 | -39.2875 | 40.5612
2005-02-19 | 22:59 | 106 | 8.4 | -45.7 | 56 | 221 | 673.6 | 221 | -38.7938 | 44.5107
2005-02-19 | 23:59 | 94 | 7.2 | -46.1 | 55 | 221 | 673.8 | 221 | -39.1938 | 44.4018
2005-02-20 | 0:59 | 86 | 8.7 | -45.9 | 54 | 209 | 673.9 | 218 | -39.0875 | 43.8276
2005-02-20 | 1:59 | 107 | 7.8 | -46.3 | 54 | 216 | 674 | 217 | -39.5187 | 43.5113
2005-02-20 | 2:59 | 108 | 7.8 | -46.1 | 54 | 215 | 674 | 216 | -39.35 | 43.3557
2005-02-20 | 3:59 | 97 | 8 | -46.3 | 54 | 218 | 674 | 215 | -39.5812 | 43.0937
2005-02-20 | 4:59 | 95 | 9 | -45.9 | 54 | 220 | 674.2 | 219 | -39.0562 | 44.0371
2005-02-20 | 5:59 | 97 | 8.5 | -46 | 55 | 212 | 674.2 | 165 | -40.8438 | 32.8153
2005-02-20 | 6:59 | 96 | 8.8 | -46.1 | 55 | 221 | 674.6 | 202 | -39.7875 | 40.4367
2005-02-20 | 7:59 | 94 | 10.2 | -46.2 | 55 | 220 | 674.8 | 221 | -39.2938 | 44.3746
2005-02-20 | 8:59 | 96 | 9.2 | -46.3 | 55 | 219 | 674.9 | 218 | -39.4875 | 43.7202
2005-02-20 | 9:59 | 94 | 9 | -46.3 | 55 | 217 | 675 | 218 | -39.4875 | 43.7202
2005-02-20 | 10:59 | 89 | 8.9 | -46.3 | 55 | 213 | 675.1 | 215 | -39.5812 | 43.0937
2005-02-20 | 11:59 | 93 | 8.4 | -46.8 | 54 | 153 | 675.5 | 200 | -40.55 | 39.8485
2005-02-20 | 12:59 | 91 | 6.8 | -46.7 | 55 | 169 | 675.5 | 170 | -41.3875 | 33.6958
2005-02-20 | 13:59 | 89 | 6.2 | -45.5 | 56 | 142 | 675.8 | 144 | -41 | 28.6111
2005-02-20 | 14:59 | 86 | 8.2 | -46.1 | 56 | 177 | 675.9 | 150 | -41.4125 | 29.727
2005-02-20 | 15:59 | 75 | 9.1 | -45.9 | 56 | 181 | 676 | 183 | -40.1812 | 36.5445
2005-02-20 | 16:59 | 79 | 8 | -46.3 | 56 | 161 | 676.1 | 181 | -40.6437 | 36.042
2005-02-20 | 17:59 | 81 | 8.3 | -46 | 56 | 152 | 676.5 | 159 | -41.0312 | 31.5853
2005-02-20 | 18:59 | 74 | 9 | -45.9 | 56 | 182 | 676.8 | 160 | -40.9 | 31.8098
2005-02-20 | 19:59 | 71 | 9.8 | -46 | 56 | 160 | 676.9 | 174 | -40.5625 | 34.6655
2005-02-20 | 20:59 | 75 | 9.3 | -46 | 56 | 155 | 677 | 165 | -40.8438 | 32.8153
2005-02-20 | 21:59 | 74 | 8.7 | -46 | 56 | 177 | 677.4 | 182 | -40.3125 | 36.3154
2005-02-20 | 22:59 | 76 | 10.5 | -46.5 | 56 | 178 | 677.7 | 170 | -41.1875 | 33.7377
2005-02-20 | 23:59 | 71 | 9.6 | -46.5 | 56 | 147 | 678 | 191 | -40.5312 | 38.0597
2005-02-21 | 0:59 | 79 | 7.7 | -46.7 | 56 | 203 | 678.2 | 183 | -40.9813 | 36.3641
2005-02-21 | 1:59 | 73 | 8.4 | -47.1 | 55 | 207 | 678.3 | 205 | -40.6938 | 40.8084
2005-02-21 | 2:59 | 83 | 8.2 | -46.7 | 55 | 212 | 678.5 | 210 | -40.1375 | 41.9476
2005-02-21 | 3:59 | 84 | 10.1 | -47.1 | 55 | 215 | 678.5 | 212 | -40.475 | 42.259
2005-02-21 | 4:59 | 96 | 7.4 | -46.9 | 55 | 217 | 678.7 | 216 | -40.15 | 43.1428
2005-02-21 | 5:59 | 98 | 7.4 | -46.1 | 56 | 135 | 678.6 | 170 | -40.7875 | 33.8215
2005-02-21 | 6:59 | 96 | 9.6 | -46.1 | 56 | 219 | 678.7 | 200 | -39.85 | 40.021
2005-02-21 | 7:59 | 99 | 9.4 | -46.1 | 55 | 217 | 678.7 | 218 | -39.2875 | 43.7739
2005-02-21 | 8:59 | 92 | 9.2 | -45.7 | 55 | 214 | 678.6 | 214 | -39.0125 | 43.0432
2005-02-21 | 9:59 | 98 | 8.1 | -46 | 54 | 212 | 678.7 | 213 | -39.3438 | 42.7552
2005-02-21 | 10:59 | 92 | 9.7 | -46.1 | 54 | 207 | 678.7 | 209 | -39.5688 | 41.8943
2005-02-21 | 11:59 | 93 | 11 | -46 | 54 | 202 | 678.5 | 204 | -39.625 | 40.8779
2005-02-21 | 12:59 | 102 | 13.2 | -45.9 | 54 | 196 | 678.4 | 199 | -39.6812 | 39.8622
2005-02-21 | 13:59 | 97 | 11.1 | -46.1 | 53 | 191 | 678.4 | 194 | -40.0375 | 38.7755
2005-02-21 | 14:59 | 92 | 10.9 | -46.4 | 53 | 186 | 678 | 189 | -40.4937 | 37.6699
2005-02-21 | 15:59 | 107 | 8.4 | -46 | 54 | 182 | 677.9 | 184 | -40.25 | 36.7286
2005-02-21 | 16:59 | 102 | 10.4 | -45.9 | 54 | 179 | 677.6 | 180 | -40.275 | 35.9246
2005-02-21 | 17:59 | 101 | 12 | -45.8 | 55 | 179 | 677.3 | 179 | -40.2062 | 35.7402
2005-02-21 | 18:59 | 95 | 11.7 | -46 | 55 | 180 | 677.2 | 179 | -40.4062 | 35.6961
2005-02-21 | 19:59 | 101 | 11.6 | -46.2 | 55 | 179 | 677.2 | 179 | -40.6063 | 35.652
2005-02-21 | 20:59 | 113 | 10.4 | -46.3 | 55 | 180 | 676.8 | 177 | -40.7687 | 35.2182
2005-02-21 | 21:59 | 105 | 10.7 | -45.9 | 55 | 183 | 676.5 | 181 | -40.2437 | 36.1312
2005-02-21 | 22:59 | 72 | 3.1 | -46.3 | 54 | 187 | 676.4 | 185 | -40.5187 | 36.867
2005-02-21 | 23:59 | 106 | 9.7 | -46.5 | 54 | 191 | 676 | 189 | -40.5938 | 37.6466
2005-02-22 | 0:59 | 112 | 9.9 | -46.6 | 54 | 196 | 675.6 | 194 | -40.5375 | 38.656
2005-02-22 | 1:59 | 90 | 8.7 | -46.5 | 54 | 200 | 675.3 | 198 | -40.3125 | 39.5079
2005-02-22 | 2:59 | 90 | 10.5 | -46.3 | 54 | 205 | 674.8 | 203 | -39.9562 | 40.5947
2005-02-22 | 3:59 | M | M | M | M | M | M | 206 | 0 | 0 |  | BAD Data Point
2005-02-22 | 5:59 | 103 | 7.2 | -47.4 | 53 | 138 | 673.6 | 152 | -42.65 | 29.8916
2005-02-22 | 6:59 | 107 | 7.7 | -47.5 | 53 | 212 | 673.5 | 192 | -41.5 | 38.0298
2005-02-22 | 7:59 | 88 | 6.2 | -47.4 | 53 | 211 | 673.3 | 212 | -40.775 | 42.1806
2005-02-22 | 8:59 | 87 | 9.5 | -47.3 | 53 | 208 | 672.9 | 208 | -40.8 | 41.3784
2005-02-22 | 9:59 | 61 | 6.3 | -47.6 | 53 | 205 | 672.8 | 207 | -41.1313 | 41.0949
2005-02-22 | 10:59 | 71 | 6.1 | -47.9 | 53 | 201 | 672.7 | 203 | -41.5562 | 40.1945
2005-02-22 | 11:59 | 59 | 6.1 | -48.3 | 53 | 195 | 672.5 | 198 | -42.1125 | 39.0688
2005-02-22 | 12:59 | 73 | 7 | -48.7 | 53 | 190 | 672.4 | 193 | -42.6688 | 37.95
2005-02-22 | 13:59 | 83 | 5 | -48.9 | 53 | 185 | 672.2 | 187 | -43.0562 | 36.6809
2005-02-22 | 14:59 | 80 | 8.7 | -48.9 | 53 | 181 | 671.9 | 183 | -43.1812 | 35.8681
2005-02-22 | 15:59 | 75 | 8.5 | -48.8 | 53 | 177 | 671.8 | 179 | -43.2062 | 35.0786
2005-02-22 | 16:59 | 64 | 7.3 | -49.1 | 53 | 174 | 671.9 | 174 | -43.6625 | 34.001
2005-02-22 | 17:59 | 74 | 7.9 | -49.4 | 53 | 164 | 672 | 162 | -44.3375 | 31.5213
2005-02-22 | 18:59 | 61 | 9.3 | -49.2 | 53 | 161 | 672.1 | 167 | -43.9813 | 32.5675
2005-02-22 | 19:52 | 46 | 9.7 | -48.9 | 53 | 162 | 672.2 | 165 | -43.7437 | 32.2258
2005-02-22 | 20:59 | 46 | 8.3 | -48.2 | 53 | 167 | 672.6 | 163 | -43.1063 | 31.9632
2005-02-22 | 21:59 | 52 | 7.6 | -49.3 | 52 | 148 | 672.7 | 160 | -44.3 | 31.1396
2005-02-22 | 22:59 | 41 | 6.5 | -49 | 53 | 202 | 673 | 145 | -44.4688 | 28.1901
2005-02-22 | 23:59 | 48 | 8.9 | -48.5 | 53 | 187 | 673 | 159 | -43.5312 | 31.0956
2005-02-23 | 0:59 | 48 | 7.6 | -49.5 | 52 | 200 | 673.3 | 181 | -43.8438 | 35.3284
2005-02-23 | 1:59 | 42 | 7.3 | -48.3 | 53 | 157 | 673.5 | 159 | -43.3312 | 31.1347
2005-02-23 | 2:59 | 25 | 12.1 | -47.7 | 54 | 167 | 673.6 | 174 | -42.2625 | 34.3011
2005-02-23 | 3:59 | 32 | 10.6 | -47.7 | 54 | 212 | 673.8 | 183 | -41.9813 | 36.1387
2005-02-23 | 4:59 | 33 | 9.5 | -48 | 53 | 199 | 674.2 | 191 | -42.0312 | 37.7067
2005-02-23 | 5:59 | 34 | 7.7 | -47.9 | 53 | 203 | 674.7 | 160 | -42.9 | 31.4156
2005-02-23 | 6:59 | 33 | 9.8 | -47.9 | 53 | 131 | 675.1 | 166 | -42.7125 | 32.632
2005-02-23 | 7:59 | 34 | 9.7 | -48 | 53 | 211 | 675.7 | 155 | -43.1562 | 30.3849
2005-02-23 | 8:59 | 34 | 8.4 | -48.5 | 52 | 192 | 676 | 192 | -42.5 | 37.7933
2005-02-23 | 9:59 | 28 | 12.2 | -48.6 | 52 | 198 | 676 | 192 | -42.6 | 37.7696
2005-02-23 | 10:59 | 13 | 8.8 | -48.8 | 52 | 152 | 676.7 | 195 | -42.7062 | 38.3343
2005-02-23 | 11:59 | 17 | 11.6 | -48.6 | 52 | 190 | 676.8 | 128 | -44.6 | 24.8644
2005-02-23 | 12:59 | 18 | 12.9 | -49 | 51 | 189 | 677.3 | 187 | -43.1562 | 36.6579
2005-02-23 | 13:59 | 5 | 10.4 | -49.6 | 51 | 98 | 677.9 | 151 | -44.8813 | 29.2799
2005-02-23 | 14:59 | 4 | 10.9 | -49.4 | 51 | 154 | 678.2 | 143 | -44.9312 | 27.7198
2005-02-23 | 15:59 | 3 | 11.2 | -49.6 | 51 | 163 | 678.7 | 153 | -44.8188 | 29.6794
2005-02-23 | 16:59 | 358 | 9.3 | -50.1 | 51 | 113 | 679.1 | 142 | -45.6625 | 27.398
2005-02-23 | 17:59 | 2 | 11.6 | -49.9 | 51 | 122 | 679.6 | 163 | -44.8062 | 31.6218
2005-02-23 | 18:59 | 8 | 11.8 | -49.9 | 51 | 134 | 680.1 | 152 | -45.15 | 29.4234
2005-02-23 | 19:59 | 7 | 12.3 | -49.9 | 51 | 126 | 680.6 | 133 | -45.7437 | 25.6482
2005-02-23 | 20:59 | 5 | 11.9 | -49.8 | 51 | 151 | 681.2 | 130 | -45.7375 | 25.0707
2005-02-23 | 21:59 | 6 | 10.5 | -49.9 | 51 | 154 | 681.5 | 146 | -45.3375 | 28.2283
2005-02-23 | 22:59 | 9 | 11.1 | -50.1 | 51 | 95 | 681.9 | 144 | -45.6 | 27.795
2005-02-23 | 23:59 | 8 | 10.3 | -49.4 | 52 | 139 | 682.4 | 119 | -45.6812 | 22.9576
2005-02-24 | 0:59 | 10 | 12.4 | -49.5 | 52 | 199 | 682.6 | 135 | -45.2812 | 26.1108
2005-02-24 | 1:59 | 2 | 14.3 | -48.9 | 53 | 222 | 682.8 | 204 | -42.525 | 40.1491
2005-02-24 | 2:59 | 6 | 12 | -48.4 | 53 | 179 | 683 | 188 | -42.525 | 37.0001
2005-02-24 | 3:59 | 6 | 11.5 | -48.4 | 53 | 189 | 683.3 | 169 | -43.1187 | 33.1371
2005-02-24 | 4:59 | 4 | 12.6 | -48.4 | 53 | 126 | 683.8 | 172 | -43.025 | 33.7452
2005-02-24 | 5:59 | 6 | 10.8 | -48.1 | 53 | 125 | 684.2 | 126 | -44.1625 | 24.5438
2005-02-24 | 6:59 | 10 | 10.7 | -48.2 | 53 | 205 | 684.5 | 155 | -43.3563 | 30.3467
2005-02-24 | 7:59 | 6 | 10.2 | -48.3 | 53 | 87 | 684.8 | 128 | -44.3 | 24.9117
2005-02-24 | 8:59 | 9 | 9.2 | -47.7 | 54 | 111 | 685.1 | 103 | -44.4813 | 20.0231
2005-02-24 | 9:59 | 13 | 11.9 | -47.2 | 54 | 90 | 685.3 | 104 | -43.95 | 20.2856
2005-02-24 | 10:59 | 9 | 9.9 | -46.5 | 55 | 129 | 685.8 | 124 | -42.625 | 24.3891
2005-02-24 | 11:59 | 6 | 10.7 | -45.7 | 55 | 115 | 686.1 | 127 | -41.7313 | 25.119
2005-02-24 | 12:59 | 5 | 10.4 | -45.3 | 56 | 92 | 686.5 | 96 | -42.3 | 18.9203
2005-02-24 | 13:59 | 16 | 10.1 | -45.7 | 56 | 121 | 686.6 | 103 | -42.4813 | 20.2769
2005-02-24 | 14:59 | 20 | 9 | -46.4 | 55 | 109 | 686.9 | 112 | -42.9 | 21.9909
2005-02-24 | 15:59 | 18 | 11.9 | -46.3 | 55 | 107 | 687.1 | 114 | -42.7375 | 22.4064
2005-02-24 | 16:59 | 19 | 12.6 | -45.9 | 55 | 142 | 687.4 | 118 | -42.2125 | 23.2689
2005-02-24 | 17:59 | 18 | 11.2 | -46.3 | 55 | 113 | 687.6 | 124 | -42.425 | 24.4196
2005-02-24 | 18:59 | 15 | 12.3 | -46.3 | 55 | 159 | 687.9 | 123 | -42.4562 | 24.2179
2005-02-24 | 19:59 | 19 | 13.5 | -46.7 | 55 | 142 | 688.1 | 152 | -41.95 | 30.0227
2005-02-24 | 20:59 | 17 | 14.1 | -46.8 | 55 | 141 | 688.3 | 134 | -42.6125 | 26.358
2005-02-24 | 21:59 | 21 | 14.6 | -47.2 | 54 | 165 | 688.7 | 148 | -42.575 | 29.1186
2005-02-24 | 22:59 | 26 | 12.2 | -46.3 | 55 | 148 | 689.1 | 162 | -41.2375 | 32.1401
2005-02-24 | 23:59 | 40 | 10.1 | -46.8 | 54 | 142 | 689.4 | 157 | -41.8937 | 31.0211
2005-02-25 | 0:59 | 42 | 11.2 | -47.3 | 53 | 172 | 689.6 | 165 | -42.1437 | 32.551
2005-02-25 | 1:59 | 47 | 9 | -47.7 | 53 | 174 | 689.8 | 173 | -42.2938 | 34.0973
2005-02-25 | 2:59 | 46 | 10.6 | -47.3 | 53 | 155 | 690 | 166 | -42.1125 | 32.7547
2005-02-25 | 3:59 | 36 | 12.7 | -47 | 53 | 177 | 690.1 | 173 | -41.5938 | 34.2465
2005-02-25 | 4:59 | 32 | 13.1 | -46.8 | 54 | 181 | 690.3 | 180 | -41.175 | 35.725
2005-02-25 | 5:59 | 39 | 11.5 | -46.7 | 54 | 132 | 690.5 | 137 | -42.4188 | 26.9808
2005-02-25 | 6:59 | 46 | 11.8 | -47.1 | 53 | 180 | 690.8 | 168 | -41.85 | 33.2037
2005-02-25 | 7:59 | 47 | 12.9 | -47.1 | 53 | 185 | 691.2 | 182 | -41.4125 | 36.0687
2005-02-25 | 8:59 | 50 | 12.1 | -47.5 | 53 | 181 | 691.4 | 182 | -41.8125 | 35.979
2005-02-25 | 9:59 | 53 | 12 | -47.2 | 53 | 176 | 691.7 | 179 | -41.6063 | 35.4315
2005-02-25 | 10:59 | 54 | 12.1 | -47.4 | 53 | 174 | 691.7 | 176 | -41.9 | 34.7739
2005-02-25 | 11:59 | 65 | 9.6 | -48.5 | 52 | 169 | 691.8 | 172 | -43.125 | 33.724
2005-02-25 | 12:59 | 70 | 11.7 | -48.4 | 52 | 164 | 692 | 166 | -43.2125 | 32.5297
2005-02-25 | 13:59 | 67 | 10.8 | -48.2 | 52 | 162 | 692.1 | 163 | -43.1063 | 31.9632
2005-02-25 | 14:59 | 58 | 12.2 | -48.1 | 52 | 156 | 692 | 159 | -43.1313 | 31.1739
2005-02-25 | 15:59 | 67 | 11.9 | -47.6 | 52 | 150 | 691.9 | 152 | -42.85 | 29.8541
2005-02-25 | 16:59 | 56 | 13.5 | -47.6 | 52 | 148 | 691.9 | 149 | -42.9438 | 29.2477
2005-02-25 | 17:59 | 58 | 13.5 | -47.6 | 53 | 146 | 691.9 | 147 | -43.0063 | 28.8438
2005-02-25 | 18:59 | 63 | 11.7 | -47.8 | 53 | 146 | 691.9 | 146 | -43.2375 | 28.606
2005-02-25 | 19:59 | 65 | 14 | -47.6 | 53 | 146 | 691.7 | 146 | -43.0375 | 28.642
2005-02-25 | 20:59 | 66 | 14.3 | -47.4 | 53 | 145 | 691.5 | 145 | -42.8687 | 28.4759
2005-02-25 | 21:59 | 66 | 13.8 | -47.9 | 53 | 150 | 691.4 | 148 | -43.275 | 28.991
2005-02-25 | 22:59 | 69 | 12.8 | -48.2 | 53 | 155 | 691.3 | 152 | -43.45 | 29.7418
2005-02-25 | 23:59 | 65 | 16.4 | -47.7 | 53 | 157 | 690.8 | 156 | -42.825 | 30.6446
2005-02-26 | 0:59 | 59 | 14.4 | -47.3 | 53 | 154 | 690.6 | 157 | -42.3937 | 30.9244
2005-02-26 | 1:59 | 57 | 11.9 | -47.2 | 53 | 156 | 690.5 | 155 | -42.3563 | 30.5377
2005-02-26 | 2:59 | 56 | 15.4 | -46.6 | 54 | 158 | 689.9 | 155 | -41.7563 | 30.6522
2005-02-26 | 3:59 | 59 | 15.7 | -46.5 | 54 | 163 | 689.5 | 160 | -41.5 | 31.6915
2005-02-26 | 4:59 | 59 | 15.4 | -46.3 | 54 | 157 | 689.2 | 161 | -41.2687 | 31.9355
2005-02-26 | 5:59 | 65 | 17.9 | -46.1 | 54 | 91 | 688.6 | 127 | -42.1313 | 25.0564
2005-02-26 | 6:59 | 57 | 16.9 | -45.8 | 55 | 147 | 688.3 | 140 | -41.425 | 27.743
2005-02-26 | 7:59 | 54 | 18.1 | -45.6 | 55 | 147 | 687.9 | 147 | -41.0063 | 29.206
2005-02-26 | 8:59 | 61 | 16.2 | -45.3 | 55 | 134 | 687.5 | 142 | -40.8625 | 28.2378
2005-02-26 | 9:59 | 45 | 16.4 | -44.4 | 56 | 123 | 687.2 | 132 | -40.275 | 26.3447
2005-02-26 | 10:59 | 52 | 17 | -44.1 | 57 | 136 | 686.8 | 127 | -40.1313 | 25.3693
2005-02-26 | 11:59 | 46 | 16 | -43.9 | 57 | 129 | 686.4 | 129 | -39.8687 | 25.8105
2005-02-26 | 12:59 | 51 | 14.5 | -43.8 | 57 | 125 | 686 | 122 | -39.9875 | 24.3921
2005-02-26 | 13:59 | 48 | 15.9 | -43.3 | 58 | 72 | 685.4 | 114 | -39.7375 | 22.8277
2005-02-26 | 14:59 | 47 | 13.9 | -42.9 | 58 | 124 | 685 | 122 | -39.0875 | 24.5274
2005-02-26 | 15:59 | 46 | 17.7 | -43 | 58 | 121 | 684.6 | 120 | -39.25 | 24.1013
2005-02-26 | 16:59 | 44 | 17.2 | -42.7 | 58 | 132 | 684.2 | 119 | -38.9813 | 23.9398
2005-02-26 | 17:59 | 44 | 15.5 | -42.4 | 59 | 112 | 683.9 | 108 | -39.025 | 21.7211
2005-02-26 | 18:59 | 44 | 14.4 | -42.5 | 59 | 97 | 683.7 | 99 | -39.4062 | 19.8645
2005-02-26 | 19:59 | 44 | 16.7 | -42.1 | 59 | 88 | 683.5 | 103 | -38.8813 | 20.7337
2005-02-26 | 20:59 | 38 | 18.8 | -41.9 | 59 | 122 | 683 | 120 | -38.15 | 24.2639
2005-02-26 | 21:59 | 41 | 14.9 | -42 | 59 | 115 | 683 | 123 | -38.1562 | 24.8696
2005-02-26 | 22:59 | 43 | 15.2 | -41.4 | 60 | 155 | 682.8 | 118 | -37.7125 | 23.9231
2005-02-26 | 23:59 | 36 | 16.8 | -41 | 60 | 115 | 682.4 | 111 | -37.5312 | 22.5287
2005-02-27 | 0:59 | 41 | 16.1 | -41.7 | 60 | 83 | 682.4 | 77 | -39.2938 | 15.4608
2005-02-27 | 1:59 | 36 | 13.7 | -41.6 | 59 | 145 | 682.7 | 111 | -38.1313 | 22.4467
2005-02-27 | 2:59 | 38 | 13.5 | -41.5 | 59 | 192 | 682.5 | 132 | -37.375 | 26.8163
2005-02-27 | 3:59 | 22 | 14 | -40 | 61 | 76 | 682.5 | 129 | -35.9688 | 26.4304
2005-02-27 | 4:59 | 28 | 14 | -40.2 | 61 | 61 | 682.6 | 84 | -37.575 | 17.0442
2005-02-27 | 5:59 | 26 | 17 | -40.3 | 61 | 74 | 682.7 | 100 | -37.175 | 20.34
2005-02-27 | 6:59 | 30 | 17.5 | -40.5 | 61 | 94 | 683 | 90 | -37.6875 | 18.2492
2005-02-27 | 7:59 | 27 | 13.8 | -41.1 | 60 | 85 | 683.4 | 119 | -37.3813 | 24.1744
2005-02-27 | 8:59 | 30 | 14.7 | -40.4 | 61 | 82 | 683.7 | 106 | -37.0875 | 21.5719
2005-02-27 | 9:59 | 31 | 16.6 | -39.7 | 61 | 61 | 683.9 | 76 | -37.325 | 15.4444
2005-02-27 | 10:59 | 29 | 15.3 | -39 | 62 | 70 | 684.3 | 61 | -37.0938 | 12.4135
2005-02-27 | 11:59 | 26 | 15 | -39.2 | 62 | 69 | 684.8 | 81 | -36.6688 | 16.526
2005-02-27 | 12:59 | 15 | 19.3 | -38.3 | 63 | 153 | 685.2 | 79 | -35.8312 | 16.1994
2005-02-27 | 13:59 | 16 | 17.9 | -38.4 | 62 | 83 | 685.7 | 100 | -35.275 | 20.5741
2005-02-27 | 14:59 | 11 | 16.4 | -38.9 | 62 | 77 | 686.2 | 91 | -36.0562 | 18.6349
2005-02-27 | 15:59 | 9 | 17 | -38.8 | 62 | 79 | 686.8 | 102 | -35.6125 | 20.9432
2005-02-27 | 16:59 | 8 | 15.3 | -39 | 62 | 78 | 687.6 | 75 | -36.6562 | 15.303
2005-02-27 | 17:59 | 1 | 14.6 | -38.6 | 62 | 64 | 688.3 | 95 | -35.6313 | 19.5037
2005-02-27 | 18:59 | 5 | 15.9 | -39.3 | 62 | 100 | 688.9 | 86 | -36.6125 | 17.552
2005-02-27 | 19:59 | 10 | 16.1 | -39.1 | 62 | 96 | 689.7 | 83 | -36.5063 | 16.9506
2005-02-27 | 20:59 | 6 | 15.6 | -39.5 | 62 | 81 | 690.4 | 119 | -35.7812 | 24.409
2005-02-27 | 21:59 | 8 | 14.4 | -39.5 | 62 | 63 | 691.1 | 76 | -37.125 | 15.4631
2005-02-27 | 22:59 | 13 | 15.4 | -39.4 | 62 | 109 | 691.5 | 100 | -36.275 | 20.4509
2005-02-27 | 23:59 | 9 | 13.9 | -39.1 | 62 | 95 | 692.1 | 101 | -35.9438 | 20.6966
2005-02-28 | 0:59 | 6 | 14.2 | -38.1 | 63 | 88 | 692.6 | 116 | -34.475 | 23.9803
2005-02-28 | 1:59 | 11 | 12.8 | -38.5 | 63 | 107 | 693 | 104 | -35.25 | 21.4003
2005-02-28 | 2:59 | 14 | 13.1 | -38.3 | 63 | 120 | 693.2 | 100 | -35.175 | 20.5864
2005-02-28 | 3:59 | 5 | 11.6 | -38.9 | 63 | 109 | 693.6 | 100 | -35.775 | 20.5125
2005-02-28 | 4:59 | 13 | 11.3 | -40.3 | 62 | 194 | 693.9 | 104 | -37.05 | 21.1697
2005-02-28 | 5:59 | 21 | 11.7 | -40.8 | 62 | 50 | 694.2 | 116 | -37.175 | 23.5944
2005-02-28 | 6:59 | 19 | 12.2 | -40.1 | 62 | 73 | 694.4 | 136 | -35.85 | 27.8845
2005-02-28 | 7:59 | 16 | 8.4 | -39.7 | 62 | 100 | 694.6 | 102 | -36.5125 | 20.8301
2005-02-28 | 8:59 | 29 | 13 | -39.4 | 63 | 89 | 694.3 | 95 | -36.4312 | 19.4101
2005-02-28 | 9:59 | 17 | 9.8 | -39.9 | 62 | 121 | 694.6 | 109 | -36.4937 | 22.2621
2005-02-28 | 10:59 | 25 | 12.9 | -39.7 | 62 | 131 | 694.4 | 121 | -35.9188 | 24.7987
2005-02-28 | 11:59 | 25 | 12 | -39.3 | 62 | 73 | 694.3 | 110 | -35.8625 | 22.5519
2005-02-28 | 12:59 | 33 | 11.1 | -39 | 63 | 57 | 694.2 | 75 | -36.6562 | 15.303
2005-02-28 | 13:59 | 40 | 8.5 | -39.7 | 62 | 88 | 694 | 80 | -37.2 | 16.2696
2005-02-28 | 14:59 | 36 | 12.2 | -39 | 62 | 119 | 693.5 | 103 | -35.7812 | 21.1271
2005-02-28 | 15:59 | 35 | 12.7 | -38.9 | 62 | 104 | 693.2 | 96 | -35.9 | 19.6772
2005-02-28 | 16:59 | 21 | 12.3 | -38.8 | 63 | 111 | 693 | 89 | -36.0187 | 18.2294
2005-02-28 | 17:59 | 17 | 13.7 | -38.4 | 63 | 81 | 692.6 | 83 | -35.8062 | 17.0222
2005-02-28 | 18:59 | 11 | 11.6 | -38.3 | 63 | 74 | 692.5 | 96 | -35.3 | 19.7482
2005-02-28 | 19:59 | 8 | 15.4 | -37.8 | 64 | 93 | 692.3 | 95 | -34.8312 | 19.5974
2005-02-28 | 20:59 | 29 | 6.7 | -37.8 | 64 | 107 | 692.3 | 89 | -35.0187 | 18.3391
2005-02-28 | 21:59 | 27 | 7.3 | -38.6 | 63 | 110 | 691.9 | 94 | -35.6625 | 19.2948
2005-02-28 | 22:59 | 25 | 10.4 | -39.3 | 62 | 73 | 691.6 | 124 | -35.425 | 25.489
2005-02-28 | 23:58 | 46 | 7.3 | -40.4 | 62 | 111 | 691.5 | 79 | -37.9312 | 15.995
2005-03-01 | 0:59 | 29 | 11.7 | -38.4 | 63 | 146 | 690.9 | 131 | -34.3062 | 27.1084
2005-03-01 | 1:59 | 43 | 11.5 | -39.4 | 62 | 78 | 690.4 | 94 | -36.4625 | 19.2022
2005-03-01 | 2:59 | 50 | 10.3 | -39 | 62 | 95 | 689.9 | 90 | -36.1875 | 18.4155
2005-03-01 | 3:59 | 51 | 10.7 | -40 | 61 | 56 | 689.4 | 82 | -37.4375 | 16.6523
2005-03-01 | 4:59 | 53 | 11.2 | -41.9 | 59 | 166 | 688.9 | 100 | -38.775 | 20.1429
2005-03-01 | 5:59 | 48 | 11.6 | -40 | 61 | 73 | 688.5 | 100 | -36.875 | 20.377
2005-03-01 | 6:59 | 39 | 11.1 | -38.2 | 63 | 68 | 688 | 72 | -35.95 | 14.7535
2005-03-01 | 7:59 | 44 | 14.3 | -39.7 | 61 | 104 | 687.5 | 95 | -36.7313 | 19.375
2005-03-01 | 8:59 | 51 | 12.2 | -40.4 | 60 | 160 | 687.3 | 126 | -36.4625 | 25.7391
2005-03-01 | 9:59 | 39 | 12.6 | -40.6 | 60 | 178 | 686.9 | 168 | -35.35 | 34.549
2005-03-01 | 10:59 | 25 | 16.7 | -40.3 | 60 | 170 | 686.3 | 179 | -34.7062 | 36.9531
2005-03-01 | 11:59 | 27 | 14.5 | -40.6 | 60 | 135 | 686.2 | 156 | -35.725 | 32.0091
2005-03-01 | 12:59 | 46 | 14.1 | -40.8 | 59 | 137 | 686 | 153 | -36.0187 | 31.3382
2005-03-01 | 13:59 | 34 | 13.3 | -40.5 | 60 | 158 | 685.6 | 154 | -35.6875 | 31.6059
2005-03-01 | 14:59 | 30 | 17.6 | -40.4 | 60 | 115 | 684.9 | 132 | -36.275 | 26.9952
2005-03-01 | 15:59 | 26 | 21.2 | -40.7 | 60 | 114 | 684.6 | 114 | -37.1375 | 23.1929
2005-03-01 | 16:59 | 25 | 19.7 | -40.9 | 60 | 98 | 684.4 | 107 | -37.5562 | 21.7136
2005-03-01 | 17:59 | 27 | 18.4 | -40.8 | 61 | 98 | 684.3 | 90 | -37.9875 | 18.2159
2005-03-01 | 18:59 | 27 | 19.3 | -41 | 60 | 119 | 684.2 | 99 | -37.9062 | 20.0475
2005-03-01 | 19:59 | 36 | 15.9 | -41.5 | 60 | 85 | 684 | 104 | -38.25 | 21.0159
2005-03-01 | 20:59 | 29 | 15.2 | -42.1 | 60 | 38 | 683.7 | 76 | -39.725 | 15.2197
2005-03-01 | 21:59 | 24 | 19.6 | -41.5 | 61 | 36 | 683.3 | 46 | -40.0625 | 9.1928
2005-03-01 | 22:59 | 18 | 19.8 | -40.3 | 61 | 130 | 683.3 | 98 | -37.2375 | 19.9257
2005-03-01 | 23:59 | 14 | 19.9 | -40.2 | 61 | 100 | 683.1 | 145 | -35.6688 | 29.7621
2005-03-02 | 0:59 | 12 | 21 | -40.4 | 61 | 98 | 682.8 | 130 | -36.3375 | 26.5762
2005-03-02 | 1:59 | 16 | 18.9 | -40.6 | 61 | 138 | 682.9 | 97 | -37.5688 | 19.6828
2005-03-02 | 2:59 | 17 | 15.3 | -40.7 | 61 | 147 | 683 | 108 | -37.325 | 21.9473
2005-03-02 | 3:59 | 19 | 18.6 | -38 | 63 | 72 | 682.9 | 103 | -34.7812 | 21.254
2005-03-02 | 4:59 | 17 | 14.7 | -38.3 | 63 | 54 | 683.2 | 66 | -36.2375 | 13.5007
2005-03-02 | 5:59 | 26 | 13.5 | -39.1 | 62 | 78 | 683.1 | 82 | -36.5375 | 16.7432
2005-03-02 | 6:59 | 17 | 15.7 | -39.8 | 61 | 70 | 682.9 | 86 | -37.1125 | 17.4991
2005-03-02 | 7:59 | 32 | 13 | -40.3 | 61 | 136 | 683.1 | 120 | -36.55 | 24.5004
2005-03-02 | 8:59 | 26 | 13.6 | -40.9 | 60 | 133 | 683.1 | 132 | -36.775 | 26.9139
2005-03-02 | 9:59 | 34 | 14.1 | -41.4 | 59 | 129 | 683.1 | 133 | -37.2437 | 27.041
2005-03-02 | 10:59 | 47 | 13.6 | -41.6 | 59 | 117 | 683.1 | 125 | -37.6938 | 25.3452
2005-03-02 | 11:59 | 34 | 14.1 | -41.5 | 59 | 103 | 683.2 | 116 | -37.875 | 23.4944
2005-03-02 | 12:59 | 11 | 17.9 | -41.3 | 60 | 113 | 683.2 | 112 | -37.8 | 22.6946
2005-03-02 | 13:59 | 17 | 15.7 | -41.6 | 59 | 105 | 683.3 | 110 | -38.1625 | 22.2402
2005-03-02 | 14:59 | 43 | 9.8 | -42 | 59 | 105 | 683.7 | 107 | -38.6562 | 21.5686
2005-03-02 | 15:59 | 38 | 13.6 | -41.9 | 59 | 96 | 683.7 | 100 | -38.775 | 20.1429
2005-03-02 | 16:59 | 21 | 20.6 | -41.4 | 59 | 99 | 683.3 | 97 | -38.3687 | 19.5872
2005-03-02 | 17:59 | 31 | 17.7 | -41.7 | 59 | 97 | 683.5 | 98 | -38.6375 | 19.7567
2005-03-02 | 18:59 | 41 | 12.5 | -42.2 | 59 | 95 | 683.9 | 97 | -39.1688 | 19.4916
2005-03-02 | 19:59 | 35 | 14.6 | -42.2 | 59 | 95 | 683.7 | 94 | -39.2625 | 18.8779
2005-03-02 | 20:59 | 34 | 14.7 | -41.8 | 60 | 92 | 683.8 | 93 | -38.8937 | 18.7193
2005-03-02 | 21:59 | 26 | 12.4 | -42 | 60 | 99 | 683.9 | 97 | -38.9688 | 19.5155
2005-03-02 | 22:59 | 23 | 18.1 | -42 | 60 | 106 | 684 | 103 | -38.7812 | 20.7464
2005-03-02 | 23:59 | 24 | 11.1 | -42.3 | 59 | 96 | 684.6 | 105 | -39.0187 | 21.1185
2005-03-03 | 0:59 | 27 | 15.9 | -42.1 | 59 | 110 | 684.3 | 105 | -38.8188 | 21.1444
2005-03-03 | 1:59 | 27 | 15.5 | -42.3 | 59 | 109 | 684.6 | 109 | -38.8937 | 21.9398
2005-03-03 | 2:59 | 14 | 18.8 | -42.3 | 59 | 118 | 684.5 | 110 | -38.8625 | 22.1454
2005-03-03 | 3:59 | 16 | 17.7 | -42.3 | 59 | 123 | 684.1 | 119 | -38.5812 | 23.9985
2005-03-03 | 4:59 | 19 | 18 | -42.1 | 59 | 122 | 684 | 124 | -38.225 | 25.0612
2005-03-03 | 5:59 | 17 | 17.9 | -42.2 | 59 | 50 | 684.5 | 103 | -38.9813 | 20.721
2005-03-03 | 6:59 | 46 | 8.7 | -42.8 | 58 | 121 | 685.1 | 118 | -39.1125 | 23.7196
2005-03-03 | 7:59 | 38 | 13.5 | -42.7 | 58 | 129 | 684.9 | 127 | -38.7313 | 25.5884
2005-03-03 | 8:59 | 36 | 13.7 | -42.6 | 58 | 129 | 685 | 128 | -38.6 | 25.8105
2005-03-03 | 9:59 | 38 | 15.1 | -42.8 | 58 | 116 | 685.2 | 122 | -38.9875 | 24.5424
2005-03-03 | 10:59 | 42 | 13.1 | -42.8 | 58 | 114 | 685.5 | 109 | -39.3937 | 21.8727
2005-03-03 | 11:59 | 39 | 13.4 | -42.9 | 58 | 117 | 685.7 | 117 | -39.2437 | 23.4996
2005-03-03 | 12:59 | 37 | 17.8 | -42.7 | 58 | 112 | 685.6 | 115 | -39.1063 | 23.1174
2005-03-03 | 13:59 | 46 | 12.8 | -42.2 | 58 | 108 | 685.7 | 110 | -38.7625 | 22.1589
2005-03-03 | 14:59 | 51 | 14.1 | -42.5 | 58 | 102 | 685.4 | 105 | -39.2188 | 21.0927
2005-03-03 | 15:59 | 35 | 14.4 | -42.4 | 58 | 97 | 685.3 | 99 | -39.3062 | 19.8767
2005-03-03 | 16:59 | 64 | 9.6 | -43.1 | 57 | 94 | 685.4 | 95 | -40.1313 | 18.977
2005-03-03 | 17:59 | 60 | 11 | -43.7 | 57 | 93 | 685.4 | 93 | -40.7938 | 18.5016
2005-03-03 | 18:59 | 37 | 15.9 | -42.3 | 59 | 94 | 685.1 | 93 | -39.3937 | 18.662
2005-03-03 | 19:59 | 48 | 13.1 | -41.7 | 59 | 95 | 685.3 | 94 | -38.7625 | 18.9358
2005-03-03 | 20:59 | 39 | 15.6 | -42.2 | 58 | 97 | 685.4 | 95 | -39.2313 | 19.0824
2005-03-03 | 21:59 | 65 | 11.3 | -44.2 | 57 | 102 | 685.4 | 100 | -41.075 | 19.8596
2005-03-03 | 22:59 | 71 | 10.7 | -45 | 57 | 108 | 685.4 | 105 | -41.7188 | 20.7693
2005-03-03 | 23:59 | 57 | 14.2 | -44.3 | 57 | 115 | 685.3 | 111 | -40.8312 | 22.0774
2005-03-04 | 0:59 | 57 | 13.8 | -44.1 | 57 | 121 | 685.1 | 118 | -40.4125 | 23.5306
2005-03-04 | 1:59 | 66 | 10.5 | -45.1 | 56 | 128 | 685 | 125 | -41.1938 | 24.8062
2005-03-04 | 2:59 | 67 | 12.3 | -45.2 | 56 | 133 | 684.7 | 131 | -41.1063 | 26.011
2005-03-04 | 3:59 | 68 | 12.8 | -45 | 56 | 137 | 684.6 | 135 | -40.7812 | 26.8593
2005-03-04 | 4:59 | 72 | 9.1 | -45.6 | 56 | 140 | 684.6 | 139 | -41.2563 | 27.5737
2005-03-04 | 5:59 | 76 | 9.4 | -46.1 | 55 | 20 | 684.4 | 111 | -42.6313 | 21.8313
2005-03-04 | 6:59 | 79 | 14.2 | -45.5 | 56 | 141 | 684.2 | 133 | -41.3438 | 26.3692
2005-03-04 | 7:59 | 81 | 11.8 | -45.5 | 56 | 138 | 684 | 140 | -41.125 | 27.7948
2005-03-04 | 8:59 | 90 | 11 | -45.6 | 56 | 130 | 683.9 | 136 | -41.35 | 26.9629
2005-03-04 | 9:59 | 81 | 12.1 | -45.4 | 56 | 129 | 683.7 | 132 | -41.275 | 26.1821
2005-03-04 | 10:59 | 81 | 13.7 | -44.8 | 57 | 122 | 683.5 | 126 | -40.8625 | 25.056
2005-03-04 | 11:59 | 90 | 10.2 | -44.8 | 57 | 113 | 683.6 | 118 | -41.1125 | 23.4288
2005-03-04 | 12:59 | 68 | 13.7 | -43.9 | 58 | 109 | 683.1 | 111 | -40.4312 | 22.1321
2005-03-04 | 13:59 | 88 | 8.5 | -44.2 | 58 | 100 | 683.1 | 106 | -40.8875 | 21.0756
2005-03-04 | 14:59 | 92 | 9 | -44 | 58 | 94 | 682.7 | 97 | -40.9688 | 19.2765
2005-03-04 | 15:59 | 85 | 14.1 | -43.5 | 59 | 89 | 682.4 | 92 | -40.625 | 18.3218
2005-03-04 | 16:59 | 81 | 14.4 | -43.6 | 59 | 86 | 682.1 | 88 | -40.85 | 17.5008
2005-03-04 | 17:59 | 80 | 13.1 | -43.3 | 59 | 83 | 681.9 | 86 | -40.6125 | 17.1282
2005-03-04 | 18:59 | 78 | 12.9 | -43.2 | 59 | 87 | 681.8 | 85 | -40.5438 | 16.9363
2005-03-04 | 19:59 | 102 | 11.9 | -44.6 | 58 | 87 | 681.8 | 86 | -41.9125 | 16.9905
2005-03-04 | 20:59 | 98 | 11.8 | -44.1 | 59 | 68 | 681.6 | 80 | -41.6 | 15.8359
2005-03-04 | 21:59 | 76 | 9.5 | -44.9 | 58 | 94 | 681.5 | 87 | -42.1812 | 17.1592
2005-03-04 | 22:59 | 81 | 14.2 | -43.7 | 59 | 99 | 681.2 | 96 | -40.7 | 19.1095
2005-03-04 | 23:59 | 83 | 11.9 | -44.2 | 59 | 105 | 681 | 102 | -41.0125 | 20.2646
2005-03-05 | 0:59 | 80 | 14.2 | -44.3 | 58 | 109 | 680.7 | 108 | -40.925 | 21.4683
2005-03-05 | 1:59 | 83 | 14.9 | -44.7 | 57 | 114 | 680.6 | 110 | -41.2625 | 21.8201
2005-03-05 | 2:59 | 84 | 9.8 | -45.5 | 56 | 123 | 680.6 | 117 | -41.8438 | 23.1249
2005-03-05 | 3:59 | 90 | 9.7 | -46.3 | 55 | 125 | 680.4 | 122 | -42.4875 | 24.0164
2005-03-05 | 4:59 | 78 | 3.6 | -47.1 | 54 | 127 | 680.7 | 126 | -43.1625 | 24.699
2005-03-05 | 5:59 | 82 | 9.9 | -47.3 | 54 | 33 | 680.5 | 99 | -44.2062 | 19.2791
2005-03-05 | 6:59 | 73 | 12.4 | -47.7 | 53 | 129 | 680.4 | 121 | -43.9188 | 23.6061
2005-03-05 | 7:59 | 86 | 9.8 | -48.4 | 53 | 125 | 680.4 | 127 | -44.4312 | 24.6965
2005-03-05 | 8:59 | 83 | 8.6 | -48.9 | 52 | 112 | 680.4 | 123 | -45.0562 | 23.824
2005-03-05 | 9:59 | 78 | 11.1 | -48.8 | 52 | 119 | 680.3 | 122 | -44.9875 | 23.6406
2005-03-05 | 10:59 | 73 | 12.3 | -48.6 | 52 | 113 | 680.2 | 116 | -44.975 | 22.4797
2005-03-05 | 11:59 | 68 | 11.8 | -48.2 | 53 | 103 | 680.2 | 108 | -44.825 | 20.9494
2005-03-05 | 12:59 | 76 | 10.6 | -48.5 | 53 | 95 | 680.3 | 99 | -45.4062 | 19.1327
2005-03-05 | 13:59 | 67 | 13.1 | -48.6 | 53 | 90 | 680.2 | 92 | -45.725 | 17.7437
2005-03-05 | 14:59 | 65 | 9.8 | -48.7 | 52 | 84 | 680 | 87 | -45.9813 | 16.7519
2005-03-05 | 15:59 | 76 | 10.3 | -49.2 | 52 | 79 | 680.1 | 81 | -46.6688 | 15.528
2005-03-05 | 16:59 | 78 | 10 | -49.9 | 51 | 76 | 680.1 | 77 | -47.4937 | 14.683
2005-03-05 | 17:59 | 84 | 10.3 | -50.1 | 51 | 68 | 680.3 | 74 | -47.7875 | 14.0841
2005-03-05 | 18:59 | 73 | 8.6 | -49.6 | 52 | 71 | 680.4 | 70 | -47.4125 | 13.3551
2005-03-05 | 19:59 | 73 | 12.1 | -49.6 | 52 | 64 | 680.4 | 71 | -47.3813 | 13.5487
2005-03-05 | 20:59 | 67 | 11.2 | -49.3 | 52 | 80 | 680.6 | 73 | -47.0187 | 13.9629
2005-03-05 | 21:59 | 68 | 11.5 | -49.7 | 52 | 80 | 680.8 | 79 | -47.2313 | 15.0899
2005-03-05 | 22:59 | 57 | 13 | -49 | 53 | 85 | 680.8 | 81 | -46.4688 | 15.548
2005-03-05 | 23:59 | 55 | 13.1 | -48.5 | 53 | 88 | 680.9 | 86 | -45.8125 | 16.5773
2005-03-06 | 0:59 | 68 | 9.2 | -49.5 | 52 | 91 | 681.1 | 90 | -46.6875 | 17.2513
2005-03-06 | 1:59 | 55 | 12.6 | -48.5 | 53 | 95 | 681 | 93 | -45.5938 | 17.9517
2005-03-06 | 2:59 | 49 | 18 | -46.8 | 54 | 98 | 680.9 | 97 | -43.7687 | 18.9419
2005-03-06 | 3:59 | 49 | 15.9 | -47.1 | 54 | 91 | 681.2 | 94 | -44.1625 | 18.3104
2005-03-06 | 4:59 | 53 | 11.8 | -47.8 | 53 | 106 | 681.4 | 103 | -44.5812 | 20.0104
2005-03-06 | 5:59 | 42 | 13.8 | -47.4 | 54 | 53 | 681.5 | 83 | -44.8062 | 16.1019
2005-03-06 | 6:59 | 51 | 12.8 | -47.4 | 54 | 104 | 681.7 | 98 | -44.3375 | 19.0685
2005-03-06 | 7:59 | 42 | 15.7 | -46.8 | 54 | 107 | 681.8 | 103 | -43.5812 | 20.1373
2005-03-06 | 8:59 | 46 | 12.2 | -47.3 | 54 | 92 | 682 | 104 | -44.05 | 20.2728
2005-03-06 | 9:59 | 49 | 12.4 | -47.8 | 53 | 91 | 682.2 | 97 | -44.7687 | 18.8224
2005-03-06 | 10:59 | 39 | 15 | -47.1 | 54 | 89 | 682.3 | 90 | -44.2875 | 17.5174
2005-03-06 | 11:59 | 39 | 16.9 | -47.3 | 54 | 47 | 682.7 | 63 | -45.3312 | 12.1812
2005-03-06 | 12:59 | 41 | 13 | -47.8 | 54 | 41 | 683.1 | 67 | -45.7062 | 12.9236
2005-03-06 | 13:59 | 34 | 13.2 | -48.2 | 53 | 61 | 683.1 | 60 | -46.325 | 11.5277
2005-03-06 | 14:59 | 32 | 14.5 | -48.4 | 53 | 31 | 683.3 | 64 | -46.4 | 12.2903
2005-03-06 | 15:59 | 35 | 15.1 | -48.5 | 53 | 84 | 683.5 | 52 | -46.875 | 9.9554
2005-03-06 | 16:59 | 26 | 14.6 | -49 | 52 | 66 | 683.7 | 71 | -46.7812 | 13.6012
2005-03-06 | 17:59 | 26 | 15.6 | -49.2 | 52 | 68 | 684 | 66 | -47.1375 | 12.6144
2005-03-06 | 18:59 | 27 | 16.3 | -49.4 | 52 | 71 | 684.2 | 67 | -47.3062 | 12.7916
2005-03-06 | 19:59 | 35 | 14.8 | -49.4 | 52 | 71 | 684.7 | 76 | -47.025 | 14.5362
2005-03-06 | 20:59 | 30 | 15.2 | -49.2 | 52 | 69 | 685 | 69 | -47.0438 | 13.1957
2005-03-06 | 21:59 | 37 | 11.1 | -49.7 | 52 | 80 | 685.3 | 80 | -47.2 | 15.284
2005-03-06 | 22:59 | 38 | 13.4 | -49.8 | 52 | 56 | 685.4 | 75 | -47.4562 | 14.305
2005-03-06 | 23:59 | 49 | 11.9 | -50.3 | 51 | 84 | 685.7 | 74 | -47.9875 | 14.0659
2005-03-07 | 0:59 | 57 | 9.6 | -51.7 | 49 | 87 | 685.7 | 84 | -49.075 | 15.8541
2005-03-07 | 1:59 | 50 | 11.5 | -50.3 | 51 | 92 | 685.7 | 89 | -47.5187 | 16.9685
2005-03-07 | 2:59 | 44 | 10.5 | -50.4 | 51 | 79 | 685.7 | 85 | -47.7437 | 16.1823
2005-03-07 | 3:59 | 41 | 12.6 | -49.2 | 52 | 87 | 685.6 | 77 | -46.7938 | 14.7494
2005-03-07 | 4:59 | 40 | 12.7 | -49.1 | 52 | 89 | 685.6 | 83 | -46.5063 | 15.9281
2005-03-07 | 5:59 | 36 | 12 | -48.8 | 52 | 50 | 685.9 | 69 | -46.6437 | 13.2297
2005-03-07 | 6:59 | 38 | 12.8 | -48.6 | 53 | 73 | 686 | 81 | -46.0688 | 15.5879
2005-03-07 | 7:59 | 31 | 14.6 | -48 | 53 | 66 | 686 | 63 | -46.0312 | 12.1268
2005-03-07 | 8:59 | 27 | 14.4 | -47.9 | 54 | 68 | 686 | 59 | -46.0562 | 11.3551
2005-03-07 | 9:59 | 30 | 16.5 | -47.7 | 54 | 64 | 685.8 | 60 | -45.825 | 11.5646
2005-03-07 | 10:59 | 28 | 14.1 | -47.2 | 54 | 86 | 686.1 | 104 | -43.95 | 20.2856
2005-03-07 | 11:59 | 42 | 12.4 | -47.8 | 54 | 61 | 686.2 | 79 | -45.3312 | 15.2748
2005-03-07 | 12:59 | 54 | 10.9 | -49.1 | 52 | 68 | 686 | 67 | -47.0063 | 12.8163
2005-03-07 | 13:59 | 44 | 11 | -50 | 51 | 70 | 686 | 54 | -48.3125 | 10.2427
2005-03-07 | 14:59 | 61 | 5.5 | -51.4 | 50 | 69 | 686 | 74 | -49.0875 | 13.9656
2005-03-07 | 15:59 | 47 | 8.3 | -51.9 | 50 | 64 | 685.8 | 64 | -49.9 | 12.0143
2005-03-07 | 16:59 | 49 | 6 | -52.6 | 49 | 59 | 686.1 | 62 | -50.6625 | 11.5806
2005-03-07 | 17:59 | 56 | 8.7 | -52.8 | 49 | 59 | 686 | 61 | -50.8937 | 11.3764
2005-03-07 | 18:59 | 38 | 12.9 | -50.8 | 50 | 58 | 685.9 | 57 | -49.0187 | 10.7621
2005-03-07 | 19:59 | 34 | 11.3 | -50.2 | 51 | 93 | 686 | 64 | -48.2 | 12.1483
2005-03-07 | 20:59 | 32 | 8.7 | -50.8 | 51 | 60 | 686.3 | 74 | -48.4875 | 14.0203
2005-03-07 | 21:59 | 28 | 10.6 | -51 | 51 | 59 | 686.2 | 65 | -48.9688 | 12.2766
2005-03-07 | 22:59 | 22 | 10.5 | -51.3 | 50 | 62 | 686.4 | 67 | -49.2062 | 12.6347
2005-03-07 | 23:59 | 22 | 12.3 | -51.4 | 50 | 75 | 686.5 | 71 | -49.1812 | 13.3912
2005-03-08 | 0:59 | 25 | 9.9 | -51.3 | 50 | 49 | 686.7 | 73 | -49.0187 | 13.783
2005-03-08 | 1:59 | 30 | 9.4 | -51.8 | 50 | 79 | 686.9 | 60 | -49.925 | 11.2615
2005-03-08 | 2:59 | 29 | 10.7 | -51.8 | 50 | 53 | 686.8 | 71 | -49.5812 | 13.3562
2005-03-08 | 3:59 | 25 | 11.4 | -52.5 | 49 | 88 | 687 | 78 | -50.0625 | 14.6268
2005-03-08 | 4:59 | 37 | 9.1 | -52.3 | 49 | 54 | 687.2 | 76 | -49.925 | 14.2646
2005-03-08 | 5:59 | 25 | 13.1 | -52.3 | 49 | 35 | 687.4 | 57 | -50.5187 | 10.6568
2005-03-08 | 6:59 | 15 | 13.9 | -52.4 | 49 | 138 | 687.6 | 72 | -50.15 | 13.4939
2005-03-08 | 7:59 | 11 | 15.5 | -52.3 | 49 | 47 | 687.9 | 94 | -49.3625 | 17.7082
2005-03-08 | 8:59 | 20 | 13.8 | -52.5 | 49 | 60 | 687.9 | 63 | -50.5312 | 11.7776
2005-03-08 | 9:59 | 18 | 16.4 | -51.8 | 50 | 93 | 688.2 | 85 | -49.1437 | 16.0357
2005-03-08 | 10:59 | 22 | 15.6 | -51.5 | 50 | 48 | 688.4 | 73 | -49.2188 | 13.7651
2005-03-08 | 11:59 | 25 | 16.9 | -51.4 | 50 | 49 | 688.3 | 56 | -49.65 | 10.5297
2005-03-08 | 12:59 | 32 | 14.6 | -50.8 | 51 | 84 | 688.3 | 73 | -48.5187 | 13.828
2005-03-08 | 13:59 | 43 | 12 | -51.2 | 50 | 74 | 688.3 | 65 | -49.1688 | 12.2606
2005-03-08 | 14:59 | 40 | 11.6 | -50.9 | 51 | 67 | 688.1 | 64 | -48.9 | 12.0931
2005-03-08 | 15:59 | 42 | 12.5 | -50.7 | 51 | 49 | 688 | 60 | -48.825 | 11.3429
2005-03-08 | 16:59 | 29 | 16.4 | -50 | 51 | 66 | 687.9 | 64 | -48 | 12.1641
2005-03-08 | 17:59 | 27 | 15.7 | -49.8 | 52 | 41 | 688 | 49 | -48.2687 | 9.2969
2005-03-08 | 18:59 | 30 | 15.9 | -49.6 | 52 | 57 | 688 | 55 | -47.8813 | 10.4616
2005-03-08 | 19:59 | 23 | 14.1 | -47.6 | 54 | 55 | 687.9 | 47 | -46.1313 | 9.0412
2005-03-08 | 20:59 | 17 | 18.9 | -46.7 | 55 | 51 | 688 | 48 | -45.2 | 9.2887
2005-03-08 | 21:59 | 38 | 9.7 | -47 | 55 | 50 | 688.5 | 50 | -45.4375 | 9.661
2005-03-08 | 22:59 | 27 | 13.5 | -47.4 | 54 | 44 | 688.4 | 55 | -45.6812 | 10.6106
2005-03-08 | 23:59 | 19 | 17.1 | -47.3 | 54 | 54 | 688.6 | 55 | -45.5812 | 10.6174
2005-03-09 | 0:59 | 30 | 5.5 | -47.3 | 55 | 61 | 689.2 | 53 | -45.6437 | 10.2272
2005-03-09 | 1:59 | 30 | 13.5 | -47.7 | 54 | 76 | 689.3 | 72 | -45.45 | 13.9108
2005-03-09 | 2:59 | 30 | 14 | -47.4 | 54 | 80 | 689.2 | 74 | -45.0875 | 14.3303
2005-03-09 | 3:59 | 47 | 10.4 | -47.8 | 54 | 80 | 689.5 | 77 | -45.3937 | 14.8822
2005-03-09 | 4:59 | 34 | 13.3 | -47.4 | 54 | 33 | 689.6 | 79 | -44.9312 | 15.3137
2005-03-09 | 5:59 | 35 | 13.7 | -46.6 | 55 | 43 | 689.7 | 58 | -44.7875 | 11.2533
2005-03-09 | 6:59 | 30 | 12.7 | -44.9 | 57 | 41 | 689.9 | 42 | -43.5875 | 8.211
2005-03-09 | 7:59 | 47 | 12.2 | -44.2 | 57 | 31 | 690.2 | 39 | -42.9813 | 7.6536
2005-03-09 | 8:59 | 73 | 11.7 | -48.2 | 54 | 58 | 690.3 | 50 | -46.6375 | 9.5871
2005-03-09 | 9:59 | 83 | 8.9 | -49.7 | 53 | 28 | 690.4 | 44 | -48.325 | 8.3452
2005-03-09 | 10:59 | 82 | 9.3 | -48 | 54 | 35 | 690.2 | 33 | -46.9688 | 6.314
2005-03-09 | 11:59 | 58 | 8.4 | -44.5 | 57 | 39 | 690 | 37 | -43.3438 | 7.2446
2005-03-09 | 12:59 | 53 | 13.2 | -42 | 60 | 35 | 689.7 | 38 | -40.8125 | 7.5589
2005-03-09 | 13:59 | 42 | 12 | -40.5 | 61 | 37 | 689.5 | 36 | -39.375 | 7.2248
2005-03-09 | 14:59 | 31 | 14.2 | -41 | 61 | 38 | 689.3 | 37 | -39.8438 | 7.4042
2005-03-09 | 15:59 | 32 | 13 | -42.6 | 59 | 45 | 689.2 | 37 | -41.4438 | 7.3312
2005-03-09 | 16:59 | 49 | 8.3 | -45.3 | 57 | 49 | 689.2 | 48 | -43.8 | 9.3714
2005-03-09 | 17:59 | 43 | 10 | -45.2 | 57 | 51 | 689.1 | 50 | -43.6375 | 9.7719
2005-03-09 | 18:59 | 50 | 9.7 | -47.2 | 55 | 48 | 688.9 | 49 | -45.6688 | 9.4539
2005-03-09 | 19:59 | 52 | 8.4 | -49.8 | 53 | 46 | 688.7 | 48 | -48.3 | 9.1053
2005-03-09 | 20:59 | 50 | 7.9 | -49.1 | 53 | 47 | 688.4 | 47 | -47.6313 | 8.9544
2005-03-09 | 21:59 | 49 | 8.3 | -47.5 | 55 | 51 | 688.2 | 50 | -45.9375 | 9.6303
2005-03-09 | 22:59 | 49 | 8.1 | -49.5 | 53 | 56 | 687.9 | 51 | -47.9062 | 9.6992
2005-03-09 | 23:59 | 73 | 8.8 | -49 | 53 | 43 | 687.7 | 49 | -47.4688 | 9.3452
2005-03-10 | 0:59 | 60 | 9.9 | -48.9 | 53 | 46 | 687.2 | 49 | -47.3687 | 9.3512
2005-03-10 | 1:59 | 56 | 11.6 | -46.5 | 56 | 39 | 686.5 | 44 | -45.125 | 8.5187
2005-03-10 | 2:59 | 67 | 12.4 | -45.1 | 57 | 39 | 686 | 39 | -43.8813 | 7.6104
2005-03-10 | 3:59 | 72 | 8.6 | -44.9 | 57 | 35 | 685.6 | 36 | -43.775 | 7.0297
2005-03-10 | 4:59 | 75 | 8.9 | -42.9 | 59 | 33 | 685.4 | 34 | -41.8375 | 6.7203
2005-03-10 | 5:59 | 79 | 9.2 | -42.2 | 60 | 39 | 685.1 | 35 | -41.1063 | 6.9495
2005-03-10 | 6:59 | 67 | 10.3 | -45.1 | 57 | 54 | 684.6 | 55 | -43.3813 | 10.7665
2005-03-10 | 7:59 | 57 | 11.3 | -45.7 | 57 | 35 | 684.3 | 39 | -44.4813 | 7.5816
2005-03-10 | 8:59 | 43 | 15 | -40.6 | 61 | 51 | 684.2 | 39 | -39.3813 | 7.8266
2005-03-10 | 9:59 | 49 | 13.8 | -43.2 | 59 | 29 | 683.9 | 58 | -41.3875 | 11.4962
2005-03-10 | 10:59 | 49 | 13.4 | -42.6 | 60 | 24 | 683.6 | 27 | -41.7563 | 5.3394
2005-03-10 | 11:59 | 51 | 13.9 | -42.3 | 60 | 22 | 683.4 | 24 | -41.55 | 4.7522
2005-03-10 | 12:59 | 46 | 12.8 | -41.7 | 61 | 30 | 683.3 | 27 | -40.8563 | 5.3694
2005-03-10 | 13:59 | 40 | 13.9 | -41.1 | 61 | 56 | 683.2 | 35 | -40.0063 | 6.9969
2005-03-10 | 14:59 | 40 | 13.5 | -42.6 | 60 | 24 | 682.9 | 46 | -41.1625 | 9.1304
2005-03-10 | 15:59 | 39 | 14 | -42.1 | 60 | 36 | 682.9 | 30 | -41.1625 | 5.9546
2005-03-10 | 16:59 | 45 | 12.6 | -42.3 | 60 | 38 | 683 | 35 | -41.2062 | 6.9452
2005-03-10 | 17:59 | 50 | 14.1 | -41.3 | 61 | 67 | 683 | 49 | -39.7687 | 9.81
2005-03-10 | 18:59 | 36 | 14.6 | -41.2 | 61 | 40 | 683 | 70 | -39.0125 | 14.0796
2005-03-10 | 19:59 | 40 | 12.9 | -42.5 | 60 | 47 | 683 | 41 | -41.2188 | 8.1352
2005-03-10 | 20:59 | 40 | 13.9 | -43.3 | 59 | 40 | 683 | 34 | -42.2375 | 6.7036
2005-03-10 | 21:59 | 41 | 12.9 | -43.8 | 59 | 52 | 683.2 | 39 | -42.5812 | 7.6729
2005-03-10 | 22:59 | 37 | 13.3 | -43.6 | 59 | 50 | 683.3 | 59 | -41.7563 | 11.6676
2005-03-10 | 23:59 | 31 | 12.9 | -44 | 58 | 47 | 683.3 | 44 | -42.625 | 8.6542
2005-03-11 | 0:59 | 34 | 12.3 | -44 | 58 | 46 | 683.3 | 44 | -42.625 | 8.6542
2005-03-11 | 1:59 | 28 | 15 | -44 | 58 | 35 | 683.4 | 36 | -42.875 | 7.0696
2005-03-11 | 2:59 | 35 | 9.9 | -43.7 | 59 | 37 | 683.3 | 36 | -42.575 | 7.0829
2005-03-11 | 3:59 | 40 | 11.3 | -44.3 | 58 | 35 | 683.1 | 26 | -43.4875 | 5.0862
2005-03-11 | 4:59 | 37 | 9.9 | -44 | 58 | 38 | 683.1 | 48 | -42.5 | 9.4483
2005-03-11 | 5:59 | 83 | 7.5 | -48 | 55 | 40 | 683.1 | 29 | -47.0938 | 5.5442
2005-03-11 | 6:59 | 56 | 9 | -47.4 | 55 | 65 | 683 | 64 | -45.4 | 12.3691
2005-03-11 | 7:59 | 51 | 8.3 | -47.3 | 55 | 46 | 682.9 | 54 | -45.6125 | 10.4223
2005-03-11 | 8:59 | 45 | 10.4 | -49.1 | 54 | 34 | 682.7 | 37 | -47.9438 | 7.0349
2005-03-11 | 9:59 | 47 | 6.4 | -48.8 | 54 | 82 | 682.5 | 57 | -47.0187 | 10.9026
2005-03-11 | 10:59 | 36 | 12.3 | -45.4 | 57 | 63 | 682.3 | 85 | -42.7437 | 16.7059
2005-03-11 | 11:59 | 38 | 11.8 | -46.7 | 56 | 33 | 682.3 | 38 | -45.5125 | 7.3389
2005-03-11 | 12:59 | 37 | 10.5 | -47.6 | 55 | 47 | 682 | 49 | -46.0688 | 9.4297
2005-03-11 | 13:59 | 37 | 10.3 | -47.5 | 55 | 42 | 681.7 | 44 | -46.125 | 8.4645
2005-03-11 | 14:59 | 37 | 10.6 | -48.2 | 54 | 27 | 681.3 | 35 | -47.1063 | 6.6908
2005-03-11 | 15:59 | 33 | 12.9 | -47.3 | 55 | 60 | 680.7 | 54 | -45.6125 | 10.4223
2005-03-11 | 16:59 | 40 | 11.8 | -48.6 | 54 | 43 | 680.4 | 46 | -47.1625 | 8.7904
2005-03-11 | 17:59 | 48 | 9.2 | -49.6 | 53 | 44 | 680.3 | 42 | -48.2875 | 7.9678
2005-03-11 | 18:59 | 45 | 8.7 | -51.9 | 51 | 27 | 679.9 | 31 | -50.9312 | 5.78
2005-03-11 | 19:59 | 43 | 10.3 | -50.7 | 52 | 45 | 679.5 | 40 | -49.45 | 7.5311
2005-03-11 | 20:59 | 41 | 8.8 | -51.7 | 50 | 49 | 679 | 43 | -50.3563 | 8.0479
2005-03-11 | 21:59 | 49 | 7.2 | -51.6 | 51 | 50 | 678.6 | 50 | -50.0375 | 9.3777
2005-03-11 | 22:59 | 31 | 12.6 | -50 | 52 | 52 | 678.2 | 53 | -48.3438 | 10.0509
2005-03-11 | 23:59 | 39 | 11.3 | -51 | 51 | 54 | 677.8 | 50 | -49.4375 | 9.4146
2005-03-12 | 0:59 | 35 | 9 | -51.3 | 51 | 49 | 677.5 | 54 | -49.6125 | 10.1562
2005-03-12 | 1:59 | 33 | 9.7 | -51.8 | 50 | 65 | 677 | 47 | -50.3312 | 8.798
2005-03-12 | 2:59 | 33 | 10.5 | -51.7 | 50 | 64 | 676.5 | 61 | -49.7938 | 11.4591
2005-03-12 | 3:59 | 26 | 12.4 | -51.7 | 50 | 46 | 676 | 58 | -49.8875 | 10.8888
2005-03-12 | 4:59 | 22 | 12.9 | -51 | 51 | 55 | 675.9 | 61 | -49.0938 | 11.5117
2005-03-12 | 5:59 | 35 | 10.1 | -51.5 | 50 | 22 | 675.9 | 43 | -50.1562 | 8.0585
2005-03-12 | 6:59 | 28 | 12.6 | -51.3 | 50 | 55 | 675.7 | 36 | -50.175 | 6.7458
2005-03-12 | 7:59 | 26 | 11.8 | -50.6 | 51 | 63 | 675.5 | 70 | -48.4125 | 13.2689
2005-03-12 | 8:59 | 24 | 11.6 | -51.2 | 51 | 33 | 675.3 | 41 | -49.9188 | 7.6957
2005-03-12 | 9:59 | 26 | 11 | -51.1 | 51 | 25 | 675.4 | 30 | -50.1625 | 5.622
2005-03-12 | 10:59 | 24 | 12.6 | -51.2 | 51 | 29 | 675.4 | 25 | -50.4188 | 4.6771
2005-03-12 | 11:59 | 19 | 12.6 | -51.5 | 50 | 36 | 675.5 | 25 | -50.7188 | 4.6679
2005-03-12 | 12:59 | 16 | 12.2 | -51.1 | 51 | 29 | 675.6 | 41 | -49.8188 | 7.7008
2005-03-12 | 13:59 | 23 | 12.5 | -51.4 | 50 | 19 | 675.4 | 29 | -50.4937 | 5.4228
2005-03-12 | 14:59 | 9 | 16.1 | -51.1 | 50 | 36 | 675.2 | 31 | -50.1313 | 5.8106
2005-03-12 | 15:59 | 12 | 17.3 | -51.1 | 51 | 20 | 675.4 | 25 | -50.3188 | 4.6802
2005-03-12 | 16:59 | 12 | 15.5 | -49.8 | 52 | 29 | 675.6 | 25 | -49.0187 | 4.7202
2005-03-12 | 17:59 | 15 | 14.7 | -50 | 52 | 37 | 676 | 47 | -48.5312 | 8.9022
2005-03-12 | 18:59 | 17 | 11.6 | -50.9 | 51 | 45 | 676.5 | 36 | -49.775 | 6.7636
2005-03-12 | 19:59 | 11 | 14.5 | -50.6 | 51 | 25 | 676.6 | 30 | -49.6625 | 5.6405
2005-03-12 | 20:59 | 9 | 15.9 | -49.6 | 52 | 13 | 676.5 | 19 | -49.0063 | 3.5877
2005-03-12 | 21:59 | 4 | 14.9 | -49.1 | 53 | 17 | 677 | 15 | -48.6313 | 2.8393
2005-03-12 | 22:59 | 10 | 14.2 | -49.4 | 52 | 22 | 677.2 | 15 | -48.9312 | 2.8338
2005-03-12 | 23:59 | 18 | 12.8 | -49.4 | 52 | 19 | 677.6 | 25 | -48.6187 | 4.7325
2005-03-13 | 0:59 | 12 | 16.6 | -49.7 | 52 | 33 | 677.7 | 29 | -48.7938 | 5.4835
2005-03-13 | 1:59 | 16 | 15 | -49.8 | 52 | 30 | 677.9 | 24 | -49.05 | 4.5305
2005-03-13 | 2:59 | 22 | 12.4 | -49.8 | 52 | 27 | 678.3 | 29 | -48.8937 | 5.4799
2005-03-13 | 3:59 | 12 | 13.1 | -49.2 | 53 | 39 | 678.3 | 29 | -48.2938 | 5.5014
2005-03-13 | 4:59 | 13 | 15 | -49.4 | 52 | 68 | 678.3 | 35 | -48.3062 | 6.639
2005-03-13 | 5:59 | 18 | 15.9 | -49 | 53 | 40 | 678.6 | 58 | -47.1875 | 11.0818
2005-03-13 | 6:59 | 15 | 15.2 | -49.5 | 53 | 28 | 679 | 35 | -48.4062 | 6.6347
2005-03-13 | 7:59 | 11 | 20.3 | -50.7 | 51 | 32 | 678.9 | 30 | -49.7625 | 5.6368
2005-03-13 | 8:59 | 15 | 17.5 | -51.2 | 51 | 41 | 679 | 37 | -50.0438 | 6.9392
2005-03-13 | 9:59 | 18 | 16.5 | -51.4 | 51 | 47 | 679.2 | 33 | -50.3687 | 6.1758
2005-03-13 | 10:59 | 23 | 13.2 | -52 | 50 | 32 | 679.7 | 37 | -50.8438 | 6.9027
2005-03-13 | 11:59 | 15 | 18.4 | -51.5 | 50 | 30 | 679.5 | 37 | -50.3438 | 6.9255
2005-03-13 | 12:59 | 14 | 18.4 | -50.9 | 51 | 45 | 679.4 | 51 | -49.3062 | 9.6112
2005-03-13 | 13:59 | 19 | 17.9 | -50.2 | 51 | 26 | 679.4 | 29 | -49.2938 | 5.4656
2005-03-13 | 14:59 | 13 | 17.2 | -49.3 | 52 | 22 | 679.5 | 23 | -48.5812 | 4.355
2005-03-13 | 15:59 | 13 | 16.7 | -48.9 | 53 | 32 | 679.5 | 29 | -47.9937 | 5.5121
2005-03-13 | 16:59 | 19 | 16.5 | -48.9 | 53 | 20 | 679.5 | 19 | -48.3062 | 3.604
2005-03-13 | 17:59 | 14 | 17.6 | -48.2 | 54 | 22 | 679.7 | 27 | -47.3563 | 5.1531
2005-03-13 | 18:59 | 14 | 16.1 | -47.9 | 54 | 41 | 680 | 36 | -46.775 | 6.8966
2005-03-13 | 19:59 | 12 | 18.3 | -48.8 | 53 | 16 | 679.9 | 24 | -48.05 | 4.5601
2005-03-13 | 20:59 | 19 | 15.9 | -48.4 | 54 | 16 | 680.1 | 16 | -47.9 | 3.043
2005-03-13 | 21:59 | 12 | 19.8 | -47.9 | 54 | 29 | 680.1 | 25 | -47.1187 | 4.7787
2005-03-13 | 22:59 | 13 | 17.5 | -47.5 | 54 | 27 | 680.3 | 28 | -46.625 | 5.3692
2005-03-13 | 23:59 | 13 | 17.1 | -47.5 | 54 | 23 | 680.4 | 20 | -46.875 | 3.829
2005-03-14 | 0:59 | 10 | 17 | -47.3 | 55 | 27 | 680.4 | 24 | -46.55 | 4.6044
2005-03-14 | 1:59 | 10 | 17.8 | -46.9 | 55 | 28 | 679.9 | 31 | -45.9312 | 5.971
2005-03-14 | 2:59 | 14 | 17.9 | -47.5 | 55 | 42 | 679.9 | 29 | -46.5938 | 5.5621
2005-03-14 | 3:59 | 14 | 15.5 | -47.7 | 54 | 34 | 679.9 | 43 | -46.3563 | 8.2598
2005-03-14 | 4:59 | 12 | 15.2 | -48.4 | 54 | 38 | 679.9 | 21 | -47.7437 | 3.998
2005-03-14 | 5:59 | 13 | 15.4 | -48.5 | 53 | 18 | 680 | 27 | -47.6562 | 5.1432
2005-03-14 | 6:59 | 16 | 14.6 | -49.1 | 53 | 49 | 680 | 28 | -48.225 | 5.314
2005-03-14 | 7:59 | 17 | 16.1 | -49.3 | 53 | 31 | 680 | 38 | -48.1125 | 7.2172
2005-03-14 | 8:59 | 13 | 15.9 | -49.7 | 52 | 44 | 679.9 | 30 | -48.7625 | 5.6737
2005-03-14 | 9:59 | 16 | 13.1 | -49.7 | 52 | 24 | 679.9 | 32 | -48.7 | 6.0545
2005-03-14 | 10:59 | 22 | 14.6 | -49.1 | 53 | 27 | 679.9 | 34 | -48.0375 | 6.4606
2005-03-14 | 11:59 | 21 | 12.5 | -49.5 | 52 | 21 | 679.7 | 29 | -48.5938 | 5.4906
2005-03-14 | 12:59 | 22 | 14.6 | -49.8 | 52 | 31 | 679.7 | 23 | -49.0812 | 4.3408
2005-03-14 | 13:59 | 16 | 14.7 | -48.8 | 53 | 35 | 679.5 | 36 | -47.675 | 6.8567
2005-03-14 | 14:59 | 25 | 11.4 | -49.1 | 53 | 15 | 679.7 | 23 | -48.3813 | 4.3607
2005-03-14 | 15:59 | 25 | 13.6 | -49.3 | 53 | 31 | 679.4 | 24 | -48.55 | 4.5453
2005-03-14 | 16:59 | 35 | 11.2 | -48.9 | 53 | 29 | 679.3 | 36 | -47.775 | 6.8523
2005-03-14 | 17:59 | 30 | 13.2 | -49.6 | 52 | 22 | 679 | 24 | -48.85 | 4.5364
2005-03-14 | 18:59 | 33 | 14.7 | -49.4 | 53 | 13 | 678.8 | 17 | -48.8687 | 3.2129
2005-03-14 | 19:59 | 35 | 11.8 | -49.3 | 52 | 13 | 678.9 | 13 | -48.8937 | 2.4565
2005-03-14 | 20:59 | 34 | 14.1 | -49.6 | 52 | 23 | 678.5 | 19 | -49.0063 | 3.5877
2005-03-14 | 21:59 | 33 | 13.8 | -48.6 | 53 | 31 | 678.2 | 30 | -47.6625 | 5.7144
2005-03-14 | 22:59 | 38 | 14.2 | -48.6 | 53 | 26 | 677.9 | 26 | -47.7875 | 4.9485
2005-03-14 | 23:59 | 36 | 14.2 | -48.6 | 53 | 21 | 677.7 | 23 | -47.8813 | 4.3748
2005-03-15 | 0:59 | 46 | 12.8 | -49.6 | 52 | 19 | 677.3 | 20 | -48.975 | 3.7773
2005-03-15 | 1:59 | 37 | 15.3 | -48.9 | 53 | 34 | 676.9 | 30 | -47.9625 | 5.7033
2005-03-15 | 2:59 | 45 | 12.2 | -49.4 | 53 | 20 | 676.6 | 26 | -48.5875 | 4.9228
2005-03-15 | 3:59 | 46 | 14.1 | -49.4 | 53 | 24 | 676.1 | 24 | -48.65 | 4.5423
2005-03-15 | 4:59 | 51 | 12.9 | -49.6 | 52 | 17 | 675.9 | 17 | -49.0688 | 3.2087
2005-03-15 | 5:59 | 56 | 10.7 | -50.5 | 51 | 11 | 675.6 | 14 | -50.0625 | 2.6253
2005-03-15 | 6:59 | 50 | 10 | -50.8 | 51 | 30 | 675.2 | 18 | -50.2375 | 3.3715
2005-03-15 | 7:59 | 52 | 12.8 | -50.7 | 51 | 32 | 674.8 | 31 | -49.7313 | 5.8259
2005-03-15 | 8:59 | 50 | 13.9 | -50.9 | 51 | 14 | 674.4 | 22 | -50.2125 | 4.1214
2005-03-15 | 9:59 | 52 | 13.7 | -51.2 | 51 | 14 | 674.2 | 19 | -50.6063 | 3.5502
2005-03-15 | 10:59 | 38 | 14.3 | -49.6 | 52 | 14 | 673.8 | 17 | -49.0688 | 3.2087
2005-03-15 | 11:59 | 38 | 16.2 | -49.7 | 52 | 15 | 673.4 | 12 | -49.325 | 2.2612
2005-03-15 | 12:59 | 46 | 15.5 | -49.6 | 52 | 29 | 673.2 | 23 | -48.8813 | 4.3465
2005-03-15 | 13:59 | 40 | 15.8 | -49.5 | 52 | 27 | 672.8 | 24 | -48.75 | 4.5394
2005-03-15 | 14:59 | 36 | 16.6 | -49.5 | 52 | 23 | 672.4 | 24 | -48.75 | 4.5394
2005-03-15 | 15:59 | 35 | 15.1 | -49.3 | 53 | 22 | 672.3 | 23 | -48.5812 | 4.355
2005-03-15 | 16:59 | 37 | 17.2 | -49.5 | 52 | 13 | 672.1 | 13 | -49.0938 | 2.4533
2005-03-15 | 17:59 | 36 | 16.1 | -49.7 | 52 | 13 | 672.2 | 13 | -49.2938 | 2.4501
2005-03-15 | 18:59 | 32 | 19.5 | -49.6 | 52 | 12 | 672.2 | 13 | -49.1938 | 2.4517
2005-03-15 | 19:59 | 36 | 16.4 | -49.1 | 53 | 22 | 672 | 18 | -48.5375 | 3.4092
2005-03-15 | 20:59 | 34 | 14 | -48.8 | 53 | 14 | 672 | 17 | -48.2687 | 3.2255
2005-03-15 | 21:59 | 34 | 17 | -48.6 | 53 | 11 | 672 | 13 | -48.1938 | 2.4677
2005-03-15 | 22:59 | 29 | 16.5 | -49.6 | 52 | 16 | 672.1 | 14 | -49.1625 | 2.6408
2005-03-15 | 23:59 | 37 | 14.5 | -50.3 | 52 | 18 | 672.2 | 17 | -49.7687 | 3.194
2005-03-16 | 0:59 | 44 | 16.5 | -50.6 | 51 | 14 | 672.2 | 16 | -50.1 | 2.9996
2005-03-16 | 1:59 | 45 | 13.2 | -51.3 | 51 | 19 | 672.3 | 23 | -50.5812 | 4.2983
2005-03-16 | 2:59 | 39 | 15.1 | -51.6 | 50 | 25 | 672.4 | 21 | -50.9438 | 3.9152
2005-03-16 | 3:59 | 45 | 11.9 | -52 | 50 | 24 | 672.7 | 23 | -51.2812 | 4.2785
2005-03-16 | 4:59 | 47 | 8.6 | -52.2 | 50 | 30 | 673 | 25 | -51.4188 | 4.6463
2005-03-16 | 5:59 | 57 | 9.5 | -52.2 | 49 | 25 | 673.3 | 24 | -51.45 | 4.4595
2005-03-16 | 6:59 | 50 | 9.4 | -51.6 | 50 | 13 | 673.5 | 27 | -50.7563 | 5.04
2005-03-16 | 7:59 | 48 | 10.4 | -51.8 | 50 | 18 | 673.7 | 18 | -51.2375 | 3.3494
2005-03-16 | 8:59 | 53 | 7.7 | -52.9 | 49 | 20 | 674 | 17 | -52.3687 | 3.1396
2005-03-16 | 9:59 | 48 | 11 | -52 | 50 | 30 | 674.2 | 32 | -51 | 5.9638
2005-03-16 | 10:59 | 55 | 6.9 | -53 | 49 | 21 | 674.5 | 20 | -52.375 | 3.6935
2005-03-16 | 11:59 | 49 | 7.9 | -53.2 | 48 | 25 | 674.9 | 24 | -52.45 | 4.43
2005-03-16 | 12:59 | 55 | 6.8 | -54.5 | 47 | 21 | 675.1 | 21 | -53.8438 | 3.8402
2005-03-16 | 13:59 | 55 | 7.3 | -55 | 47 | 25 | 675.4 | 23 | -54.2812 | 4.1935
2005-03-16 | 14:59 | 58 | 6 | -56 | 45 | 16 | 675.7 | 21 | -55.3438 | 3.8013
2005-03-16 | 15:59 | 62 | 7.2 | -56.1 | 45 | 24 | 676 | 19 | -55.5063 | 3.4355
2005-03-16 | 16:59 | 52 | 8.8 | -55.5 | 46 | 19 | 676.4 | 29 | -54.5938 | 5.2763
2005-03-16 | 17:59 | 69 | 5.9 | -56.5 | 45 | 19 | 676.7 | 14 | -56.0625 | 2.5218
2005-03-16 | 18:59 | 56 | 7.8 | -57 | 44 | 11 | 676.9 | 14 | -56.5625 | 2.5132
2005-03-16 | 19:59 | 60 | 6.9 | -57 | 44 | 16 | 677.3 | 13 | -56.5938 | 2.3332
2005-03-16 | 20:59 | 58 | 8.4 | -57.2 | 44 | 13 | 677.7 | 15 | -56.7313 | 2.6896
2005-03-16 | 21:59 | 52 | 7.9 | -56.9 | 44 | 19 | 677.9 | 15 | -56.4312 | 2.6952
2005-03-16 | 22:59 | 47 | 9.9 | -56 | 45 | 17 | 678.3 | 18 | -55.4375 | 3.2562
2005-03-16 | 23:59 | 59 | 9.6 | -56.4 | 44 | 18 | 678.6 | 17 | -55.8687 | 3.0663
2005-03-17 | 0:59 | 60 | 8.1 | -56.8 | 44 | 15 | 678.9 | 14 | -56.3625 | 2.5167
2005-03-17 | 1:59 | 60 | 8.5 | -56.6 | 44 | 17 | 679.1 | 15 | -56.1313 | 2.7007
2005-03-17 | 2:59 | 64 | 9.8 | -57.3 | 44 | 18 | 679.1 | 14 | -56.8625 | 2.508
2005-03-17 | 3:59 | 57 | 10.2 | -57.2 | 43 | 21 | 679.1 | 20 | -56.575 | 3.59
2005-03-17 | 4:59 | 59 | 8.9 | -58 | 43 | 27 | 679.5 | 22 | -57.3125 | 3.929
2005-03-17 | 5:59 | 63 | 8.8 | -57.9 | 43 | 22 | 679.9 | 26 | -57.0875 | 4.6506
2005-03-17 | 6:59 | 62 | 8.8 | -57.9 | 43 | 18 | 680.1 | 21 | -57.2437 | 3.7522
2005-03-17 | 7:59 | 53 | 9.7 | -57.3 | 43 | 20 | 680.1 | 22 | -56.6125 | 3.948
2005-03-17 | 8:59 | 53 | 8.7 | -57.9 | 43 | 12 | 680.3 | 15 | -57.4312 | 2.6767
2005-03-17 | 9:59 | 61 | 9 | -58.1 | 42 | 27 | 680.2 | 18 | -57.5375 | 3.2096
2005-03-17 | 10:59 | 46 | 8.9 | -57.7 | 43 | 20 | 680.3 | 20 | -57.075 | 3.5777
2005-03-17 | 11:59 | 47 | 9.2 | -58.2 | 42 | 14 | 680.2 | 15 | -57.7313 | 2.6711
2005-03-17 | 12:59 | 54 | 8.2 | -58.6 | 42 | 20 | 680.3 | 16 | -58.1 | 2.8419
2005-03-17 | 13:59 | 57 | 7.6 | -58.5 | 42 | 15 | 680.4 | 21 | -57.8438 | 3.7367
2005-03-17 | 14:59 | 50 | 8 | -58.4 | 42 | 15 | 680.4 | 15 | -57.9312 | 2.6674
2005-03-17 | 15:59 | 52 | 7.2 | -58.9 | 42 | 14 | 680.5 | 14 | -58.4625 | 2.4804
2005-03-17 | 16:59 | 63 | 8.2 | -58.7 | 42 | 16 | 680.5 | 15 | -58.2313 | 2.6619
2005-03-17 | 17:59 | 59 | 9 | -57.9 | 42 | 11 | 680.3 | 14 | -57.4625 | 2.4977
2005-03-17 | 18:59 | 49 | 9.1 | -58.8 | 42 | 8 | 680.4 | 9 | -58.5187 | 1.5939
2005-03-17 | 19:59 | 48 | 10.2 | -58.8 | 42 | 10 | 680.2 | 9 | -58.5187 | 1.5939
2005-03-17 | 20:59 | 60 | 9.8 | -58.9 | 41 | 11 | 680.2 | 10 | -58.5875 | 1.7702
2005-03-17 | 21:59 | 69 | 8.9 | -58.2 | 42 | 18 | 680.3 | 15 | -57.7313 | 2.6711
2005-03-17 | 22:59 | 62 | 7.7 | -57.8 | 43 | 25 | 680 | 23 | -57.0812 | 4.1141
2005-03-17 | 23:59 | 69 | 7.4 | -57.4 | 43 | 20 | 680 | 23 | -56.6812 | 4.1255
2005-03-18 | 0:59 | 75 | 8.4 | -59.2 | 41 | 17 | 679.9 | 19 | -58.6063 | 3.3629
2005-03-18 | 1:59 | 71 | 8.1 | -58.8 | 42 | 27 | 679.7 | 15 | -58.3312 | 2.66
2005-03-18 | 2:59 | 69 | 10.1 | -58.8 | 41 | 11 | 679.5 | 20 | -58.175 | 3.5506
2005-03-18 | 3:59 | 73 | 10.2 | -59.4 | 41 | 11 | 679.3 | 10 | -59.0875 | 1.764
2005-03-18 | 4:59 | 86 | 8.5 | -59.9 | 40 | 32 | 679.1 | 17 | -59.3687 | 2.993
2005-03-18 | 5:59 | 113 | 8.2 | -59.6 | 40 | 12 | 679 | 17 | -59.0688 | 2.9993
2005-03-18 | 6:59 | 80 | 9.4 | -59.8 | 40 | 10 | 678.9 | 14 | -59.3625 | 2.4649
2005-03-18 | 7:59 | 95 | 7.9 | -60 | 40 | 16 | 678.7 | 12 | -59.625 | 2.1089
2005-03-18 | 8:59 | 80 | 9.3 | -59.8 | 40 | 26 | 678.5 | 23 | -59.0812 | 4.0575
2005-03-18 | 9:59 | 91 | 7.3 | -60.1 | 40 | 16 | 678.5 | 20 | -59.475 | 3.5185
2005-03-18 | 10:59 | 92 | 8.5 | -59.9 | 40 | 19 | 678.2 | 17 | -59.3687 | 2.993
2005-03-18 | 11:59 | 83 | 9.7 | -59.8 | 40 | 14 | 677.8 | 17 | -59.2687 | 2.9951
2005-03-18 | 12:59 | 118 | 3 | -60.4 | 40 | 12 | 677.7 | 12 | -60.025 | 2.103
2005-03-18 | 13:59 | 92 | 6.9 | -61 | 39 | 13 | 677.4 | 11 | -60.6562 | 1.9192
2005-03-18 | 14:59 | 105 | 4.9 | -61.4 | 38 | 12 | 677.3 | 12 | -61.025 | 2.0882
2005-03-18 | 15:59 | 108 | 5.9 | -61.2 | 39 | 11 | 677.1 | 12 | -60.825 | 2.0912
2005-03-18 | 16:59 | 101 | 6.9 | -62 | 38 | 11 | 677.1 | 11 | -61.6562 | 1.9056
2005-03-18 | 17:59 | 101 | 6 | -61.3 | 38 | 12 | 677.1 | 11 | -60.9562 | 1.9151
2005-03-18 | 18:59 | 107 | 8.2 | -61.1 | 39 | 10 | 676.9 | 12 | -60.725 | 2.0926
2005-03-18 | 19:59 | 114 | 9.2 | -60.7 | 39 | 9 | 676.7 | 9 | -60.4188 | 1.5729
2005-03-18 | 20:59 | 95 | 8 | -61.2 | 38 | 8 | 676.5 | 8 | -60.95 | 1.3929
2005-03-18 | 21:59 | 135 | 7.6 | -61.2 | 38 | 10 | 676.5 | 10 | -60.8875 | 1.7419
2005-03-18 | 22:59 | 123 | 8.6 | -60.1 | 40 | 10 | 676.4 | 10 | -59.7875 | 1.7554
2005-03-18 | 23:59 | 95 | 11.4 | -60.5 | 39 | 10 | 676.2 | 11 | -60.1562 | 1.926
2005-03-19 | 0:59 | 107 | 9.1 | -60.8 | 39 | 12 | 676.4 | 10 | -60.4875 | 1.7468
2005-03-19 | 1:59 | 103 | 9.6 | -60.1 | 40 | 14 | 676.1 | 14 | -59.6625 | 2.4597
2005-03-19 | 2:59 | 119 | 10.3 | -59.8 | 40 | 14 | 676.3 | 14 | -59.3625 | 2.4649
2005-03-19 | 3:59 | 112 | 9.4 | -59.9 | 40 | 10 | 676.2 | 12 | -59.525 | 2.1104
2005-03-19 | 4:59 | 121 | 8.7 | -60.6 | 39 | 8 | 676.5 | 8 | -60.35 | 1.3988
2005-03-19 | 5:59 | 98 | 11.2 | -60.5 | 39 | 7 | 676.4 | 7 | -60.2812 | 1.2245
2005-03-19 | 6:59 | 102 | 9.3 | -61 | 39 | 7 | 676.4 | 7 | -60.7812 | 1.2202
2005-03-19 | 7:59 | 112 | 11.5 | -60.8 | 39 | 8 | 676.5 | 7 | -60.5812 | 1.2219
2005-03-19 | 8:59 | 104 | 10.8 | -60.6 | 39 | 9 | 676.7 | 8 | -60.35 | 1.3988
2005-03-19 | 9:59 | 133 | 6.4 | -61.5 | 38 | 10 | 677.1 | 9 | -61.2188 | 1.564
2005-03-19 | 10:59 | 100 | 7.1 | -62.5 | 37 | 9 | 677.2 | 11 | -62.1562 | 1.8989
2005-03-19 | 11:59 | 91 | 7.3 | -62.8 | 37 | 13 | 677.3 | 13 | -62.3937 | 2.2403
2005-03-19 | 12:59 | 102 | 5.6 | -62.2 | 37 | 12 | 677.4 | 13 | -61.7938 | 2.2499
2005-03-19 | 13:59 | 98 | 6.8 | -63.2 | 36 | 11 | 677.7 | 12 | -62.825 | 2.0616
2005-03-19 | 14:59 | 120 | 4.7 | -63.8 | 36 | 10 | 678 | 11 | -63.4562 | 1.8812
2005-03-19 | 15:59 | 119 | 6.9 | -63.5 | 36 | 10 | 677.9 | 10 | -63.1875 | 1.7135
2005-03-19 | 16:59 | 104 | 5.1 | -63.7 | 36 | 10 | 678.4 | 10 | -63.3875 | 1.7111
2005-03-19 | 17:59 | 106 | 5.1 | -63.5 | 36 | 9 | 678.7 | 9 | -63.2188 | 1.5418
2005-03-19 | 18:59 | 97 | 8 | -64.3 | 35 | 8 | 678.9 | 8 | -64.05 | 1.3623
2005-03-19 | 19:59 | 88 | 9.4 | -64.3 | 35 | 8 | 679.1 | 8 | -64.05 | 1.3623
2005-03-19 | 20:59 | 84 | 9.4 | -64.4 | 35 | 7 | 679.2 | 7 | -64.1813 | 1.1909
2005-03-19 | 21:59 | 86 | 7.6 | -64.6 | 34 | 11 | 679.6 | 9 | -64.3187 | 1.5296
2005-03-19 | 22:59 | 95 | 8.7 | -64.4 | 35 | 12 | 680.1 | 11 | -64.0563 | 1.8731
2005-03-19 | 23:59 | 90 | 9.1 | -64.6 | 34 | 12 | 680.5 | 12 | -64.225 | 2.0409
2005-03-20 | 0:59 | 83 | 8.3 | -65.1 | 34 | 14 | 680.7 | 13 | -64.6937 | 2.2035
2005-03-20 | 1:59 | 75 | 7.7 | -64.9 | 34 | 16 | 680.8 | 15 | -64.4313 | 2.5473
2005-03-20 | 2:59 | 80 | 7.7 | -64.6 | 34 | 20 | 681.4 | 17 | -64.0687 | 2.8945
2005-03-20 | 3:59 | 74 | 10.1 | -64.2 | 35 | 20 | 681.5 | 16 | -63.7 | 2.7315
2005-03-20 | 4:59 | 61 | 10.7 | -63.9 | 35 | 21 | 681.8 | 20 | -63.275 | 3.4249
2005-03-20 | 5:59 | 45 | 6.6 | -63.8 | 35 | 9 | 682.4 | 21 | -63.1437 | 3.5995
2005-03-20 | 6:59 | 68 | 8.2 | -64.7 | 34 | 26 | 682.7 | 24 | -63.95 | 4.0899
2005-03-20 | 7:59 | 64 | 8.3 | -62.3 | 37 | 22 | 682.7 | 26 | -61.4875 | 4.5096
2005-03-20 | 8:59 | 18 | 11.3 | -59.2 | 40 | 25 | 683 | 20 | -58.575 | 3.5407
2005-03-20 | 9:59 | 23 | 10.3 | -57.7 | 41 | 13 | 683.1 | 16 | -57.2 | 2.8597
2005-03-20 | 10:59 | 4 | 13.4 | -55.8 | 43 | 5 | 683.2 | 8 | -55.55 | 1.4461
2005-03-20 | 11:59 | 6 | 14 | -55 | 44 | 6 | 683.6 | 5 | -54.8438 | 0.90816
2005-03-20 | 12:59 | 355 | 15.1 | -54 | 46 | 5 | 683.6 | 5 | -53.8438 | 0.91432
2005-03-20 | 13:59 | 359 | 14.4 | -52.9 | 47 | 4 | 683.8 | 5 | -52.7437 | 0.9211
2005-03-20 | 14:59 | 2 | 14.2 | -51.8 | 48 | 9 | 684 | 6 | -51.6125 | 1.1137
2005-03-20 | 15:59 | 2 | 13.1 | -51.2 | 49 | 9 | 684.6 | 10 | -50.8875 | 1.8651
2005-03-20 | 16:59 | 351 | 11.4 | -50.3 | 50 | 6 | 684.9 | 6 | -50.1125 | 1.1248
2005-03-20 | 17:59 | 349 | 11.9 | -49.4 | 51 | 5 | 685.5 | 5 | -49.2437 | 0.94266
2005-03-20 | 18:59 | 351 | 13 | -48.7 | 52 | 5 | 685.9 | 4 | -48.575 | 0.75742
2005-03-20 | 19:59 | 347 | 10.6 | -48.5 | 53 | 5 | 686.2 | 5 | -48.3438 | 0.9482
2005-03-20 | 20:59 | 4 | 12.7 | -49.5 | 52 | 5 | 686.4 | 4 | -49.375 | 0.75348
2005-03-20 | 21:59 | 358 | 13.8 | -49.5 | 52 | 5 | 686.7 | 5 | -49.3438 | 0.94204
2005-03-20 | 22:59 | 359 | 14.6 | -48.6 | 53 | 4 | 686.8 | 5 | -48.4438 | 0.94759
2005-03-20 | 23:59 | 354 | 15.5 | -48 | 53 | 4 | 686.7 | 4 | -47.875 | 0.76087
2005-03-21 | 0:59 | 10 | 5.3 | -47.3 | 54 | 4 | 687.5 | 4 | -47.175 | 0.76432
2005-03-21 | 1:59 | 11 | 9.3 | -46.7 | 55 | 4 | 687.8 | 4 | -46.575 | 0.76728
2005-03-21 | 2:59 | 0 | 14 | -47.5 | 54 | 5 | 687.5 | 4 | -47.375 | 0.76334
2005-03-21 | 3:59 | 2 | 14.6 | -47.4 | 54 | 5 | 687.8 | 5 | -47.2437 | 0.95498
2005-03-21 | 4:59 | 357 | 15.9 | -48.1 | 54 | 5 | 688 | 5 | -47.9438 | 0.95067
2005-03-21 | 5:59 | 354 | 13.1 | -48.3 | 53 | 5 | 687.8 | 5 | -48.1437 | 0.94943
2005-03-21 | 6:59 | 349 | 13 | -47.1 | 54 | 5 | 687.8 | 5 | -46.9438 | 0.95683
2005-03-21 | 7:59 | 1 | 14.1 | -47.3 | 54 | 5 | 687.8 | 5 | -47.1437 | 0.95559
2005-03-21 | 8:59 | 36 | 6.5 | -48.3 | 54 | 5 | 688.3 | 5 | -48.1437 | 0.94943
2005-03-21 | 9:59 | 28 | 9 | -47.8 | 54 | 4 | 688.1 | 5 | -47.6437 | 0.95251
2005-03-21 | 10:59 | 8 | 14.9 | -47.7 | 54 | 4 | 687.7 | 5 | -47.5438 | 0.95313
2005-03-21 | 11:59 | 356 | 16.8 | -46.8 | 55 | 4 | 687.5 | 4 | -46.675 | 0.76679
2005-03-21 | 12:59 | 6 | 15.6 | -46.8 | 55 | 4 | 687 | 4 | -46.675 | 0.76679
2005-03-21 | 13:59 | 6 | 15.2 | -46 | 56 | 4 | 686.7 | 4 | -45.875 | 0.77073
2005-03-21 | 14:59 | 1 | 13.1 | -45.4 | 56 | 4 | 686.6 | 4 | -45.275 | 0.77368
2005-03-21 | 15:59 | 4 | 13.7 | -45.8 | 56 | 5 | 686.4 | 5 | -45.6437 | 0.96483
2005-03-21 | 16:59 | 1 | 14.4 | -45.4 | 56 | 5 | 686.2 | 6 | -45.2125 | 1.161
2005-03-21 | 17:59 | 20 | 14.2 | -45.9 | 56 | 4 | 685.8 | 4 | -45.775 | 0.77122
2005-03-21 | 18:59 | 28 | 9.6 | -46.1 | 56 | 7 | 685.8 | 6 | -45.9125 | 1.1558
2005-03-21 | 19:59 | 40 | 11.3 | -46.2 | 56 | 7 | 685.7 | 7 | -45.9813 | 1.3479
2005-03-21 | 20:59 | 54 | 7.4 | -47.1 | 55 | 6 | 685.6 | 6 | -46.9125 | 1.1484
2005-03-21 | 21:59 | 38 | 7.9 | -47.8 | 54 | 6 | 685.3 | 6 | -47.6125 | 1.1432
2005-03-21 | 22:59 | 18 | 12.5 | -46.5 | 55 | 5 | 684.8 | 6 | -46.3125 | 1.1529
2005-03-21 | 23:59 | 1 | 12.2 | -48.6 | 54 | 6 | 684.1 | 5 | -48.4438 | 0.94759
2005-03-22 | 0:59 | 8 | 12.4 | -48 | 54 | 8 | 683.5 | 7 | -47.7812 | 1.3323
2005-03-22 | 1:59 | 8 | 12.3 | -48.3 | 54 | 7 | 682.8 | 7 | -48.0812 | 1.3297
2005-03-22 | 2:59 | 9 | 12.2 | -47.8 | 54 | 7 | 682.3 | 7 | -47.5812 | 1.3341
2005-03-22 | 3:59 | 21 | 10.2 | -50.7 | 52 | 6 | 682 | 7 | -50.4813 | 1.309
2005-03-22 | 4:59 | 10 | 9.7 | -49 | 53 | 8 | 681.2 | 7 | -48.7812 | 1.3237
2005-03-22 | 5:59 | 71 | 9.2 | -53.8 | 48 | 9 | 680.9 | 8 | -53.55 | 1.4658
2005-03-22 | 6:59 | 70 | 8.9 | -52.7 | 49 | 9 | 680.8 | 8 | -52.45 | 1.4767
2005-03-22 | 7:59 | 45 | 8.7 | -52.3 | 49 | 13 | 680.1 | 11 | -51.9562 | 2.0371
2005-03-22 | 8:59 | 64 | 7.6 | -52 | 50 | 8 | 679.6 | 10 | -51.6875 | 1.8552
2005-03-22 | 9:59 | 19 | 6.4 | -52.1 | 49 | 7 | 678.8 | 8 | -51.85 | 1.4826
2005-03-22 | 10:59 | 69 | 7.5 | -53.9 | 48 | 5 | 678.3 | 6 | -53.7125 | 1.0982
2005-03-22 | 11:59 | 65 | 10 | -53.9 | 48 | 5 | 678.1 | 5 | -53.7437 | 0.91494
2005-03-22 | 12:59 | 76 | 8.5 | -55.3 | 46 | 5 | 677.4 | 5 | -55.1437 | 0.90631
2005-03-22 | 13:59 | 86 | 8.1 | -55.9 | 46 | 5 | 676.9 | 5 | -55.7437 | 0.90262
2005-03-22 | 14:59 | 99 | 6 | -55.7 | 46 | 5 | 676.5 | 5 | -55.5438 | 0.90385
2005-03-22 | 15:59 | 102 | 6.9 | -54.5 | 47 | 5 | 676.1 | 5 | -54.3438 | 0.91124
2005-03-22 | 16:59 | 100 | 6.6 | -54 | 47 | 5 | 675.7 | 5 | -53.8438 | 0.91432
2005-03-22 | 17:59 | 108 | 6.4 | -55.3 | 46 | 5 | 675.5 | 5 | -55.1437 | 0.90631
2005-03-22 | 18:59 | 97 | 10.4 | -56.8 | 44 | 5 | 675.1 | 5 | -56.6437 | 0.89707
2005-03-22 | 19:59 | 105 | 6 | -57.1 | 44 | 5 | 675.1 | 5 | -56.9438 | 0.89523
2005-03-22 | 20:59 | 98 | 6.3 | -57 | 44 | 5 | 674.9 | 5 | -56.8438 | 0.89584
2005-03-22 | 21:59 | 95 | 6.1 | -56.1 | 45 | 5 | 674.6 | 5 | -55.9438 | 0.90139
2005-03-22 | 22:59 | 108 | 6 | -56.1 | 45 | 5 | 674.2 | 5 | -55.9438 | 0.90139
2005-03-22 | 23:59 | 128 | 8.7 | -57.5 | 43 | 5 | 673.9 | 5 | -57.3438 | 0.89276
2005-03-23 | 0:59 | 122 | 10.8 | -56.5 | 44 | 5 | 673.9 | 5 | -56.3438 | 0.89892
2005-03-23 | 1:59 | 104 | 6.9 | -55.2 | 46 | 5 | 673.5 | 5 | -55.0438 | 0.90693
2005-03-23 | 2:59 | 113 | 7.3 | -54 | 47 | 4 | 673.5 | 4 | -53.875 | 0.7313
2005-03-23 | 3:59 | 98 | 7.7 | -55.2 | 46 | 5 | 673.2 | 4 | -55.075 | 0.72539
2005-03-23 | 4:59 | 109 | 9.4 | -55.9 | 45 | 4 | 673.3 | 4 | -55.775 | 0.72194
2005-03-23 | 5:59 | 118 | 8.3 | -54.2 | 47 | 6 | 673 | 5 | -54.0438 | 0.91309
2005-03-23 | 6:59 | 125 | 11.9 | -53.4 | 47 | 6 | 672.8 | 6 | -53.2125 | 1.1019
2005-03-23 | 7:59 | 117 | 5.9 | -54.5 | 46 | 5 | 673 | 6 | -54.3125 | 1.0937
2005-03-23 | 8:59 | 120 | 6.4 | -56.7 | 44 | 4 | 672.9 | 4 | -56.575 | 0.718
2005-03-23 | 9:59 | 126 | 7.1 | -57.4 | 43 | 4 | 673.1 | 4 | -57.275 | 0.71455
2005-03-23 | 10:59 | 108 | 8.8 | -57.7 | 43 | 4 | 673.2 | 4 | -57.575 | 0.71307
2005-03-23 | 11:59 | 88 | 8.7 | -58.2 | 43 | 4 | 673.4 | 4 | -58.075 | 0.71061
2005-03-23 | 12:59 | 104 | 7.3 | -58.7 | 42 | 4 | 673.6 | 4 | -58.575 | 0.70814
2005-03-23 | 13:59 | 111 | 8.3 | -58.9 | 42 | 4 | 673.9 | 4 | -58.775 | 0.70716
2005-03-23 | 14:59 | 102 | 7 | -59.2 | 41 | 4 | 674 | 4 | -59.075 | 0.70568
2005-03-23 | 15:59 | 108 | 6.9 | -59.6 | 41 | 4 | 674.3 | 4 | -59.475 | 0.70371
2005-03-23 | 16:59 | 111 | 7.2 | -60.3 | 40 | 4 | 675 | 4 | -60.175 | 0.70026
2005-03-23 | 17:59 | 92 | 6.3 | -60.5 | 40 | 4 | 675.3 | 4 | -60.375 | 0.69927
2005-03-23 | 18:59 | 78 | 7.3 | -60.4 | 40 | 4 | 675.7 | 4 | -60.275 | 0.69976
2005-03-23 | 19:59 | 74 | 7.3 | -60.7 | 40 | 4 | 676 | 4 | -60.575 | 0.69829
2005-03-23 | 20:59 | 81 | 8.2 | -60.8 | 39 | 4 | 676.5 | 4 | -60.675 | 0.69779
2005-03-23 | 21:59 | 86 | 7.8 | -60.9 | 39 | 4 | 677.1 | 4 | -60.775 | 0.6973
2005-03-23 | 22:59 | 76 | 3.9 | -59.7 | 40 | 3 | 677.8 | 3 | -59.6063 | 0.5273
2005-03-23 | 23:59 | 73 | 3.2 | -59.1 | 41 | 3 | 678.6 | 3 | -59.0063 | 0.52951
2005-03-24 | 0:59 | 74 | 5.6 | -59.8 | 40 | 4 | 678.8 | 4 | -59.675 | 0.70272
2005-03-24 | 1:59 | 67 | 6.6 | -60.8 | 39 | 4 | 679.2 | 4 | -60.675 | 0.69779
2005-03-24 | 2:59 | 63 | 5.6 | -61 | 39 | 3 | 679.7 | 4 | -60.875 | 0.69681
2005-03-24 | 3:59 | 72 | 5.7 | -60.8 | 39 | 3 | 680.4 | 3 | -60.7062 | 0.52323
2005-03-24 | 4:59 | 66 | 6.4 | -59.6 | 40 | 3 | 681 | 3 | -59.5063 | 0.52766
2005-03-24 | 5:59 | 66 | 5 | -58.6 | 41 | 3 | 681.4 | 3 | -58.5063 | 0.53136
2005-03-24 | 6:59 | 58 | 7.7 | -59.1 | 41 | 3 | 681.8 | 3 | -59.0063 | 0.52951
2005-03-24 | 7:59 | 69 | 5.4 | -59.7 | 40 | 3 | 682.3 | 3 | -59.6063 | 0.5273
2005-03-24 | 8:59 | 44 | 9.3 | -59.2 | 41 | 3 | 682.7 | 3 | -59.1063 | 0.52914
2005-03-24 | 9:59 | 41 | 8.9 | -58.9 | 41 | 3 | 683.1 | 3 | -58.8062 | 0.53025
2005-03-24 | 10:59 | 53 | 6.5 | -59.7 | 40 | 3 | 683.8 | 3 | -59.6063 | 0.5273
2005-03-24 | 11:59 | 44 | 7.6 | -58 | 42 | 3 | 684.1 | 3 | -57.9062 | 0.53358
2005-03-24 | 12:59 | 47 | 8.3 | -59.3 | 41 | 3 | 684.3 | 3 | -59.2062 | 0.52877
2005-03-24 | 13:59 | 44 | 8.3 | -59 | 41 | 3 | 684.9 | 3 | -58.9062 | 0.52988
2005-03-24 | 14:59 | 37 | 9 | -58.9 | 41 | 3 | 685.1 | 3 | -58.8062 | 0.53025
2005-03-24 | 15:59 | 49 | 8.6 | -58.7 | 41 | 3 | 685.6 | 3 | -58.6063 | 0.53099
2005-03-24 | 16:59 | 31 | 9.4 | -58.6 | 41 | 3 | 685.9 | 3 | -58.5063 | 0.53136
2005-03-24 | 17:59 | 39 | 8.6 | -58.7 | 41 | 2 | 686.5 | 3 | -58.6063 | 0.53099
2005-03-24 | 18:59 | 38 | 11.6 | -58.6 | 41 | 2 | 686.7 | 2 | -58.5375 | 0.35416
2005-03-24 | 19:59 | 26 | 13.3 | -58.7 | 41 | 2 | 686.9 | 2 | -58.6375 | 0.35392
2005-03-24 | 20:59 | 27 | 11.8 | -57.9 | 42 | 2 | 687.2 | 2 | -57.8375 | 0.35589
2005-03-24 | 21:59 | 29 | 12 | -58.4 | 42 | 2 | 687.5 | 2 | -58.3375 | 0.35466
2005-03-24 | 22:59 | 40 | 10.4 | -58.6 | 41 | 2 | 688 | 2 | -58.5375 | 0.35416
2005-03-24 | 23:59 | 36 | 10.4 | -59.1 | 41 | 2 | 688.3 | 2 | -59.0375 | 0.35293
2005-03-25 | 0:59 | 45 | 11 | -59.1 | 41 | 2 | 688.5 | 2 | -59.0375 | 0.35293
2005-03-25 | 1:59 | 33 | 12.5 | -57.9 | 42 | 2 | 688.6 | 2 | -57.8375 | 0.35589
2005-03-25 | 2:59 | 41 | 11.1 | -56.9 | 43 | 2 | 688.8 | 2 | -56.8375 | 0.35835
2005-03-25 | 3:59 | 34 | 12.1 | -56 | 44 | 2 | 688.8 | 2 | -55.9375 | 0.36057
2005-03-25 | 4:59 | 28 | 12.6 | -56 | 44 | 2 | 688.8 | 2 | -55.9375 | 0.36057
2005-03-25 | 5:59 | 34 | 14.2 | -55.5 | 45 | 2 | 689 | 2 | -55.4375 | 0.3618
2005-03-25 | 6:59 | 37 | 9.8 | -54.8 | 45 | 2 | 689.2 | 2 | -54.7375 | 0.36353
2005-03-25 | 7:59 | 34 | 12.1 | -53.5 | 47 | 2 | 689.1 | 2 | -53.4375 | 0.36673
2005-03-25 | 8:59 | 36 | 11.5 | -53.4 | 47 | 2 | 689 | 2 | -53.3375 | 0.36698
2005-03-25 | 9:59 | 35 | 13.3 | -53.1 | 47 | 2 | 688.9 | 2 | -53.0375 | 0.36772
2005-03-25 | 10:59 | 38 | 13.6 | -52.1 | 48 | 2 | 689.1 | 2 | -52.0375 | 0.37018
2005-03-25 | 11:59 | 26 | 15.4 | -52.4 | 48 | 2 | 689.1 | 2 | -52.3375 | 0.36944
2005-03-25 | 12:59 | 25 | 16.2 | -51.6 | 49 | 1 | 689.1 | 2 | -51.5375 | 0.37141
2005-03-25 | 13:59 | 30 | 15.2 | -51.7 | 49 | 2 | 688.9 | 2 | -51.6375 | 0.37117
2005-03-25 | 14:59 | 19 | 16.5 | -51.7 | 49 | 1 | 688.6 | 2 | -51.6375 | 0.37117
2005-03-25 | 15:59 | 27 | 18.8 | -51.5 | 49 | 1 | 688.5 | 1 | -51.4688 | 0.18579
2005-03-25 | 16:59 | 23 | 18.8 | -50.9 | 50 | 1 | 688.5 | 1 | -50.8687 | 0.18653
2005-03-25 | 17:59 | 16 | 20.6 | -50.3 | 51 | 1 | 688.1 | 1 | -50.2687 | 0.18727
2005-03-25 | 18:59 | 16 | 22.1 | -50.1 | 51 | 1 | 687.9 | 1 | -50.0688 | 0.18752
2005-03-25 | 19:59 | 16 | 22.1 | -49.8 | 51 | 1 | 687.9 | 1 | -49.7687 | 0.18788
2005-03-25 | 20:59 | 14 | 21.6 | -49.4 | 52 | 1 | 687.8 | 1 | -49.3687 | 0.18838
2005-03-25 | 21:59 | 14 | 22.9 | -49.4 | 52 | 1 | 687.5 | 1 | -49.3687 | 0.18838
2005-03-25 | 22:59 | 11 | 24.2 | -49.3 | 52 | 1 | 687.5 | 1 | -49.2687 | 0.1885
2005-03-25 | 23:59 | 16 | 21.7 | -48.6 | 53 | 1 | 687.8 | 1 | -48.5688 | 0.18936
2005-03-26 | 0:59 | 9 | 23.6 | -48.1 | 53 | 1 | 687.3 | 1 | -48.0688 | 0.18998
2005-03-26 | 1:59 | 9 | 25.1 | -48 | 53 | 1 | 687.3 | 1 | -47.9688 | 0.1901
2005-03-26 | 2:59 | 9 | 22.2 | -47.8 | 54 | 1 | 687.2 | 1 | -47.7687 | 0.19035
2005-03-26 | 3:59 | 7 | 24.2 | -47.9 | 54 | 1 | 687.3 | 1 | -47.8687 | 0.19023
2005-03-26 | 4:59 | 10 | 21.5 | -48 | 54 | 1 | 687.2 | 1 | -47.9688 | 0.1901
2005-03-26 | 5:59 | 9 | 19.7 | -48 | 54 | 1 | 687.3 | 1 | -47.9688 | 0.1901
2005-03-26 | 6:59 | 10 | 19.9 | -48.2 | 53 | 1 | 687.4 | 1 | -48.1688 | 0.18986
2005-03-26 | 7:59 | 10 | 23.9 | -48.2 | 53 | 1 | 687.1 | 1 | -48.1688 | 0.18986
2005-03-26 | 8:59 | 8 | 22.7 | -48.3 | 53 | 1 | 687.4 | 1 | -48.2687 | 0.18973
2005-03-26 | 9:59 | 7 | 22 | -48.1 | 53 | 1 | 687.5 | 1 | -48.0688 | 0.18998
2005-03-26 | 10:59 | 9 | 21.1 | -47.9 | 54 | 1 | 687.7 | 1 | -47.8687 | 0.19023
2005-03-26 | 11:59 | 2 | 19.2 | -48.2 | 53 | 1 | 687.8 | 1 | -48.1688 | 0.18986
2005-03-26 | 12:59 | 6 | 21.4 | -48.1 | 53 | 1 | 687.6 | 1 | -48.0688 | 0.18998
2005-03-26 | 13:59 | 11 | 16.5 | -48 | 54 | 1 | 687.8 | 1 | -47.9688 | 0.1901
2005-03-26 | 14:59 | 18 | 17.1 | -48.2 | 53 | 1 | 688 | 1 | -48.1688 | 0.18986
2005-03-26 | 15:59 | 13 | 21.1 | -48.2 | 53 | 1 | 687.8 | 1 | -48.1688 | 0.18986
2005-03-26 | 16:59 | 23 | 15.4 | -48.5 | 53 | 1 | 688.1 | 1 | -48.4688 | 0.18949
2005-03-26 | 17:59 | 19 | 14.8 | -48.9 | 53 | 1 | 688 | 1 | -48.8687 | 0.18899
2005-03-26 | 18:59 | 16 | 19.5 | -49.7 | 52 | 1 | 687.8 | 1 | -49.6688 | 0.18801
2005-03-26 | 19:59 | 20 | 14.7 | -50.5 | 51 | 1 | 688 | 1 | -50.4688 | 0.18702
2005-03-26 | 20:59 | 18 | 17.6 | -51.1 | 51 | 1 | 688 | 1 | -51.0688 | 0.18628
2005-03-26 | 21:59 | 27 | 12.2 | -51.4 | 50 | 1 | 688.2 | 1 | -51.3687 | 0.18591
2005-03-26 | 22:59 | 20 | 15.9 | -50.6 | 51 | 1 | 688 | 1 | -50.5688 | 0.1869
2005-03-26 | 23:59 | 19 | 17.2 | -50.4 | 51 | 1 | 688 | 1 | -50.3687 | 0.18715
2005-03-27 | 0:59 | 36 | 11.9 | -51.1 | 50 | 1 | 688.1 | 1 | -51.0688 | 0.18628
2005-03-27 | 1:59 | 28 | 15.1 | -51.4 | 50 | 1 | 688 | 1 | -51.3687 | 0.18591
2005-03-27 | 2:59 | 41 | 13.7 | -51.5 | 50 | 1 | 687.9 | 1 | -51.4688 | 0.18579
2005-03-27 | 3:59 | 51 | 10.1 | -51.7 | 50 | 1 | 687.8 | 1 | -51.6688 | 0.18554
2005-03-27 | 4:59 | 28 | 12.9 | -51.8 | 50 | 1 | 687.5 | 1 | -51.7687 | 0.18542
2005-03-27 | 5:59 | 16 | 13.7 | -52.4 | 49 | 1 | 687.3 | 1 | -52.3687 | 0.18468
2005-03-27 | 6:59 | 30 | 18.5 | -52.2 | 49 | 1 | 686.9 | 1 | -52.1688 | 0.18493
2005-03-27 | 7:59 | 26 | 18.6 | -51.8 | 49 | 1 | 686.9 | 1 | -51.7687 | 0.18542
2005-03-27 | 8:59 | 39 | 12.2 | -52.2 | 49 | 1 | 687 | 1 | -52.1688 | 0.18493
2005-03-27 | 9:59 | 49 | 12 | -52.3 | 49 | 1 | 686.8 | 1 | -52.2687 | 0.1848
2005-03-27 | 10:59 | 43 | 14.1 | -52.2 | 49 | 1 | 686.6 | 1 | -52.1688 | 0.18493
2005-03-27 | 11:59 | 29 | 12.5 | -51.9 | 49 | 1 | 686.7 | 1 | -51.8687 | 0.1853
2005-03-27 | 12:59 | 24 | 16.7 | -51.4 | 50 | 1 | 686.3 | 1 | -51.3687 | 0.18591
2005-03-27 | 13:59 | 24 | 13.7 | -51.5 | 50 | 1 | 686.2 | 1 | -51.4688 | 0.18579
2005-03-27 | 14:59 | 27 | 11.6 | -51.9 | 49 | 1 | 686 | 1 | -51.8687 | 0.1853
2005-03-27 | 15:59 | 36 | 12 | -52.7 | 49 | 1 | 685.8 | 1 | -52.6688 | 0.18431
2005-03-27 | 16:59 | 39 | 10.2 | -52.9 | 48 | 1 | 686 | 1 | -52.8687 | 0.18407
2005-03-27 | 17:59 | 40 | 10.7 | -53.5 | 48 | 1 | 686 | 1 | -53.4688 | 0.18333
2005-03-27 | 18:59 | 38 | 12.2 | -53.4 | 48 | 1 | 685.8 | 1 | -53.3687 | 0.18345
2005-03-27 | 19:59 | 30 | 10.2 | -53.2 | 48 | 1 | 685.8 | 1 | -53.1688 | 0.1837
2005-03-27 | 20:59 | 20 | 15 | -51.5 | 50 | 1 | 685.7 | 1 | -51.4688 | 0.18579
2005-03-27 | 21:59 | 16 | 13.9 | -51.8 | 49 | 1 | 685.7 | 1 | -51.7687 | 0.18542
2005-03-27 | 22:59 | 33 | 11.5 | -52.3 | 49 | 1 | 685.8 | 1 | -52.2687 | 0.1848
2005-03-27 | 23:59 | 23 | 11 | -53 | 48 | 1 | 685.7 | 1 | -52.9688 | 0.18394
2005-03-28 | 0:59 | 31 | 8.4 | -52.9 | 48 | 1 | 686 | 1 | -52.8687 | 0.18407
2005-03-28 | 1:59 | 28 | 12.4 | -52.6 | 49 | 1 | 685.5 | 1 | -52.5688 | 0.18444
2005-03-28 | 2:59 | 31 | 9.2 | -53.5 | 48 | 1 | 685.6 | 1 | -53.4688 | 0.18333
2005-03-28 | 3:59 | 28 | 8.9 | -54.2 | 47 | 1 | 685.7 | 1 | -54.1688 | 0.18246
2005-03-28 | 4:59 | 45 | 7.7 | -55.3 | 46 | 1 | 685.7 | 1 | -55.2687 | 0.18111
2005-03-28 | 5:59 | 55 | 6.8 | -54.9 | 46 | 1 | 685.8 | 1 | -54.8687 | 0.1816
2005-03-28 | 6:59 | 18 | 13.9 | -54.6 | 46 | 1 | 685.4 | 1 | -54.5688 | 0.18197
2005-03-28 | 7:59 | 44 | 9.4 | -55.4 | 46 | 1 | 685.6 | 1 | -55.3687 | 0.18099
2005-03-28 | 8:59 | 52 | 7.3 | -55.8 | 45 | 1 | 685.7 | 1 | -55.7687 | 0.18049
2005-03-28 | 9:59 | 29 | 11.4 | -54.8 | 46 | 1 | 685.5 | 1 | -54.7687 | 0.18172
2005-03-28 | 10:59 | 40 | 8.5 | -54.9 | 46 | 1 | 685.7 | 1 | -54.8687 | 0.1816
2005-03-28 | 11:59 | 86 | 7.1 | -56.8 | 44 | 1 | 685.7 | 1 | -56.7687 | 0.17926
2005-03-28 | 12:59 | 63 | 7.3 | -57.4 | 43 | 1 | 685.7 | 1 | -57.3687 | 0.17852
2005-03-28 | 13:59 | 69 | 6.9 | -59 | 42 | 1 | 685.5 | 1 | -58.9688 | 0.17655
2005-03-28 | 14:59 | 44 | 7.5 | -59.2 | 42 | 1 | 685.6 | 1 | -59.1688 | 0.1763
2005-03-28 | 15:59 | 47 | 6.4 | -56.9 | 44 | 1 | 685.4 | 1 | -56.8687 | 0.17914
2005-03-28 | 16:59 | 44 | 8.1 | -57 | 44 | 1 | 685.5 | 1 | -56.9688 | 0.17901
2005-03-28 | 17:59 | 77 | 8 | -59 | 42 | 1 | 685.8 | 1 | -58.9688 | 0.17655
2005-03-28 | 18:59 | 62 | 8.7 | -59.2 | 41 | 1 | 685.8 | 1 | -59.1688 | 0.1763
2005-03-28 | 19:59 | 57 | 10.4 | -59 | 41 | 1 | 685.4 | 1 | -58.9688 | 0.17655
2005-03-28 | 20:59 | 47 | 8.9 | -57.4 | 43 | 1 | 685.4 | 1 | -57.3687 | 0.17852
2005-03-28 | 21:59 | 108 | 4.3 | -59.5 | 41 | 0 | 685.8 | 0 | -59.5 | 0
2005-03-28 | 22:59 | 83 | 6.8 | -58.7 | 42 | 0 | 685.7 | 0 | -58.7 | 0
2005-03-28 | 23:59 | 72 | 8.2 | -58.7 | 42 | 0 | 685.7 | 0 | -58.7 | 0
2005-03-29 | 0:59 | 83 | 6.6 | -59.6 | 41 | 0 | 685.6 | 0 | -59.6 | 0
2005-03-29 | 1:59 | 81 | 8.5 | -59.7 | 40 | 0 | 685.5 | 0 | -59.7 | 0
2005-03-29 | 2:59 | 70 | 10 | -59.4 | 41 | 0 | 685.3 | 0 | -59.4 | 0
2005-03-29 | 3:59 | 73 | 6.6 | -60 | 40 | 0 | 685 | 0 | -60 | 0
2005-03-29 | 4:59 | 113 | 5.9 | -58.7 | 41 | 1 | 685.2 | 1 | -58.6688 | 0.17692
2005-03-29 | 5:59 | 85 | 7.6 | -58.5 | 42 | 1 | 685.3 | 1 | -58.4688 | 0.17717
2005-03-29 | 6:59 | 70 | 8.3 | -58.5 | 42 | 1 | 685.1 | 1 | -58.4688 | 0.17717
2005-03-29 | 7:59 | 77 | 7.9 | -59.1 | 41 | 1 | 684.9 | 1 | -59.0688 | 0.17643
2005-03-29 | 8:59 | 94 | 3.8 | -59.5 | 41 | 1 | 685.1 | 1 | -59.4688 | 0.17593
2005-03-29 | 9:59 | 75 | 4.9 | -59.6 | 40 | 1 | 685 | 1 | -59.5688 | 0.17581
2005-03-29 | 10:59 | 91 | 5.6 | -58.8 | 41 | 1 | 685.2 | 1 | -58.7687 | 0.1768
2005-03-29 | 11:59 | 80 | 5.6 | -60.4 | 40 | 1 | 685 | 0 | -60.4 | 0
2005-03-29 | 12:59 | 86 | 5 | -59.4 | 41 | 1 | 684.8 | 1 | -59.3687 | 0.17606
2005-03-29 | 13:59 | 83 | 5.2 | -59.7 | 40 | 1 | 684.7 | 1 | -59.6688 | 0.17569
2005-03-29 | 14:59 | 74 | 5.3 | -59.8 | 40 | 1 | 684.4 | 1 | -59.7687 | 0.17556
2005-03-29 | 15:59 | 71 | 5.9 | -60.2 | 40 | 1 | 684.3 | 1 | -60.1688 | 0.17507
2005-03-29 | 16:59 | 66 | 6 | -59.4 | 40 | 1 | 684.3 | 1 | -59.3687 | 0.17606
2005-03-29 | 17:59 | 79 | 5.2 | -60.4 | 39 | 1 | 684.4 | 1 | -60.3687 | 0.17483
2005-03-29 | 18:59 | 94 | 4.8 | -61 | 39 | 0 | 684.3 | 1 | -60.9688 | 0.17409
2005-03-29 | 19:59 | 120 | 4.5 | -62.1 | 38 | 0 | 684.2 | 0 | -62.1 | 0
2005-03-29 | 20:59 | 86 | 9.6 | -59.8 | 40 | 0 | 683.9 | 0 | -59.8 | 0
2005-03-29 | 21:59 | 78 | 11.2 | -60.1 | 40 | 0 | 683.7 | 0 | -60.1 | 0
2005-03-29 | 22:59 | 70 | 9.7 | -59.4 | 40 | 0 | 683.6 | 0 | -59.4 | 0
2005-03-29 | 23:59 | 93 | 9.2 | -60.9 | 39 | 0 | 683.7 | 0 | -60.9 | 0
2005-03-30 | 0:59 | 97 | 9.5 | -60.3 | 39 | 0 | 683.4 | 0 | -60.3 | 0
2005-03-30 | 1:59 | 97 | 7.8 | -60.2 | 39 | 0 | 683.3 | 0 | -60.2 | 0
2005-03-30 | 2:59 | 95 | 7.7 | -60.9 | 39 | 0 | 683 | 0 | -60.9 | 0
2005-03-30 | 3:59 | 83 | 9.4 | -60 | 40 | 0 | 682.7 | 0 | -60 | 0
2005-03-30 | 4:59 | 79 | 10.3 | -60 | 40 | 0 | 682.5 | 0 | -60 | 0
2005-03-30 | 5:59 | 112 | 3.7 | -62.5 | 37 | 0 | 682.6 | 0 | -62.5 | 0
2005-03-30 | 6:59 | 85 | 9 | -61.7 | 38 | 0 | 682.4 | 0 | -61.7 | 0
2005-03-30 | 7:59 | 96 | 8.5 | -62.5 | 37 | 0 | 682.3 | 0 | -62.5 | 0
2005-03-30 | 8:59 | 81 | 7.8 | -60.4 | 39 | 0 | 682 | 0 | -60.4 | 0
2005-03-30 | 9:59 | 126 | 0 | -62.3 | 37 | 0 | 682.2 | 0 | -62.3 | 0
2005-03-30 | 10:59 | 80 | 6.9 | -63.2 | 36 | 0 | 682 | 0 | -63.2 | 0
2005-03-30 | 11:59 | 82 | 6.4 | -62.4 | 37 | 0 | 681.8 | 0 | -62.4 | 0
2005-03-30 | 12:59 | 117 | 4.5 | -63.1 | 36 | 0 | 682 | 0 | -63.1 | 0
2005-03-30 | 13:59 | 89 | 7.7 | -62.5 | 37 | 0 | 681.7 | 0 | -62.5 | 0
2005-03-30 | 14:59 | 111 | 4.7 | -63.6 | 36 | 0 | 681.8 | 0 | -63.6 | 0
2005-03-30 | 15:59 | 137 | 2.4 | -63.3 | 36 | 0 | 681.6 | 0 | -63.3 | 0
2005-03-30 | 16:59 | 94 | 4.9 | -62.9 | 36 | 0 | 681.7 | 0 | -62.9 | 0
2005-03-30 | 17:59 | 86 | 6.7 | -62.6 | 37 | 0 | 681.7 | 0 | -62.6 | 0
2005-03-30 | 18:59 | 74 | 6 | -62.6 | 37 | 0 | 681.6 | 0 | -62.6 | 0
2005-03-30 | 19:59 | 84 | 7.9 | -63.1 | 36 | 0 | 681.5 | 0 | -63.1 | 0
2005-03-30 | 20:59 | 90 | 7.1 | -61.8 | 37 | 0 | 681.5 | 0 | -61.8 | 0
2005-03-30 | 21:59 | 100 | 5.7 | -63.2 | 36 | 0 | 681.5 | 0 | -63.2 | 0
2005-03-30 | 22:59 | 95 | 6.7 | -62.3 | 37 | 0 | 681.5 | 0 | -62.3 | 0
2005-03-30 | 23:59 | 109 | 5.7 | -62 | 37 | 0 | 681.6 | 0 | -62 | 0
2005-03-31 | 0:59 | 101 | 6.1 | -62.7 | 36 | 0 | 681.6 | 0 | -62.7 | 0
2005-03-31 | 1:59 | 97 | 6 | -62.8 | 36 | 0 | 681.3 | 0 | -62.8 | 0
2005-03-31 | 2:59 | 81 | 7.7 | -61.9 | 37 | 0 | 681.1 | 0 | -61.9 | 0
2005-03-31 | 3:59 | 97 | 5.9 | -61.8 | 37 | 0 | 681.1 | 0 | -61.8 | 0
2005-03-31 | 4:59 | 114 | 5.6 | -62.4 | 37 | 0 | 681.1 | 0 | -62.4 | 0
2005-03-31 | 5:59 | 96 | 6.8 | -64.3 | 35 | 0 | 681.1 | 0 | -64.3 | 0
2005-03-31 | 6:59 | 98 | 5.9 | -63 | 36 | 0 | 681.1 | 0 | -63 | 0
2005-03-31 | 7:59 | 108 | 4.8 | -62.1 | 37 | 0 | 681 | 0 | -62.1 | 0
2005-03-31 | 8:59 | 83 | 8.2 | -63.7 | 35 | 0 | 680.6 | 0 | -63.7 | 0
2005-03-31 | 9:59 | 103 | 6 | -64 | 35 | 0 | 680.6 | 0 | -64 | 0
2005-03-31 | 10:59 | 114 | 6.9 | -63.7 | 35 | 0 | 680.5 | 0 | -63.7 | 0
2005-03-31 | 11:59 | 97 | 5.8 | -64.7 | 34 | 0 | 680.3 | 0 | -64.7 | 0
2005-03-31 | 12:59 | 95 | 5.7 | -63.7 | 35 | 0 | 680.3 | 0 | -63.7 | 0
2005-03-31 | 13:59 | 100 | 6.3 | -63.7 | 35 | 0 | 680.1 | 0 | -63.7 | 0
2005-03-31 | 14:59 | 106 | 6.2 | -63.2 | 36 | 0 | 679.9 | 0 | -63.2 | 0
2005-03-31 | 15:59 | 102 | 5.9 | -63.3 | 35 | 0 | 679.8 | 0 | -63.3 | 0
2005-03-31 | 16:59 | 105 | 4.3 | -63.6 | 35 | 0 | 679.6 | 0 | -63.6 | 0
2005-03-31 | 17:59 | 115 | 5.4 | -62.3 | 37 | 0 | 679.7 | 0 | -62.3 | 0
2005-03-31 | 18:59 | 101 | 6.6 | -63.1 | 36 | 0 | 679.5 | 0 | -63.1 | 0
2005-03-31 | 19:59 | 93 | 8.2 | -64.2 | 35 | 0 | 679.3 | 0 | -64.2 | 0
2005-03-31 | 20:59 | 80 | 8.7 | -64.1 | 35 | 0 | 679 | 0 | -64.1 | 0
2005-03-31 | 21:59 | 74 | 10.7 | -63.2 | 35 | 0 | 678.9 | 0 | -63.2 | 0
2005-03-31 | 22:59 | 76 | 10 | -64 | 35 | 0 | 678.9 | 0 | -64 | 0
2005-03-31 | 23:59 | 97 | 6.1 | -63.1 | 36 | 0 | 678.8 | 0 | -63.1 | 0
2005-04-01 | 0:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 1:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 2:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 3:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 4:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 5:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 6:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 7:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 8:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 9:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 10:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 11:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 12:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 13:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 14:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 15:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 16:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 17:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 18:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 19:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 20:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 21:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 22:59 | [6 empty] | 0 | 0 | 0
2005-04-01 | 23:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 24:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 25:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 26:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 27:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 28:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 29:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 30:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 31:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 32:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 33:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 34:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 35:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 36:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 37:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 38:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 39:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 40:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 41:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 42:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 43:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 44:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 45:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 46:59 | [6 empty] | 0 | 0 | 0
2005-04-02 | 47:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 48:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 49:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 50:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 51:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 52:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 53:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 54:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 55:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 56:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 57:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 58:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 59:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 60:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 61:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 62:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 63:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 64:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 65:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 66:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 67:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 68:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 69:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 70:59 | [6 empty] | 0 | 0 | 0
2005-04-03 | 71:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 72:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 73:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 74:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 75:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 76:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 77:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 78:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 79:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 80:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 81:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 82:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 83:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 84:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 85:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 86:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 87:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 88:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 89:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 90:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 91:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 92:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 93:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 94:59 | [6 empty] | 0 | 0 | 0
2005-04-04 | 95:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 96:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 97:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 98:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 99:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 100:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 101:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 102:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 103:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 104:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 105:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 106:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 107:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 108:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 109:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 110:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 111:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 112:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 113:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 114:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 115:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 116:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 117:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 118:59 | [6 empty] | 0 | 0 | 0
2005-04-05 | 119:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 120:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 121:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 122:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 123:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 124:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 125:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 126:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 127:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 128:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 129:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 130:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 131:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 132:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 133:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 134:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 135:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 136:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 137:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 138:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 139:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 140:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 141:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 142:59 | [6 empty] | 0 | 0 | 0
2005-04-06 | 143:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 144:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 145:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 146:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 147:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 148:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 149:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 150:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 151:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 152:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 153:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 154:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 155:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 156:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 157:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 158:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 159:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 160:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 161:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 162:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 163:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 164:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 165:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 166:59 | [6 empty] | 0 | 0 | 0
2005-04-07 | 167:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 168:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 169:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 170:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 171:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 172:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 173:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 174:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 175:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 176:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 177:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 178:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 179:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 180:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 181:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 182:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 183:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 184:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 185:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 186:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 187:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 188:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 189:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 190:59 | [6 empty] | 0 | 0 | 0
2005-04-08 | 191:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 192:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 193:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 194:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 195:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 196:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 197:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 198:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 199:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 200:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 201:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 202:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 203:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 204:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 205:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 206:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 207:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 208:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 209:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 210:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 211:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 212:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 213:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 214:59 | [6 empty] | 0 | 0 | 0
2005-04-09 | 215:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 216:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 217:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 218:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 219:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 220:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 221:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 222:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 223:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 224:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 225:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 226:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 227:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 228:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 229:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 230:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 231:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 232:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 233:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 234:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 235:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 236:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 237:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 238:59 | [6 empty] | 0 | 0 | 0
2005-04-10 | 239:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 240:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 241:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 242:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 243:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 244:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 245:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 246:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 247:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 248:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 249:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 250:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 251:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 252:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 253:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 254:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 255:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 256:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 257:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 258:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 259:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 260:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 261:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 262:59 | [6 empty] | 0 | 0 | 0
2005-04-11 | 263:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 264:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 265:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 266:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 267:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 268:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 269:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 270:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 271:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 272:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 273:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 274:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 275:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 276:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 277:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 278:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 279:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 280:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 281:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 282:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 283:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 284:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 285:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 286:59 | [6 empty] | 0 | 0 | 0
2005-04-12 | 287:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 288:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 289:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 290:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 291:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 292:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 293:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 294:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 295:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 296:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 297:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 298:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 299:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 300:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 301:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 302:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 303:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 304:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 305:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 306:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 307:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 308:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 309:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 310:59 | [6 empty] | 0 | 0 | 0
2005-04-13 | 311:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 312:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 313:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 314:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 315:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 316:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 317:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 318:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 319:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 320:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 321:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 322:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 323:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 324:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 325:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 326:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 327:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 328:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 329:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 330:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 331:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 332:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 333:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 334:59 | [6 empty] | 0 | 0 | 0
2005-04-14 | 335:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 336:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 337:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 338:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 339:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 340:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 341:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 342:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 343:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 344:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 345:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 346:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 347:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 348:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 349:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 350:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 351:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 352:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 353:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 354:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 355:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 356:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 357:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 358:59 | [6 empty] | 0 | 0 | 0
2005-04-15 | 359:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 360:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 361:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 362:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 363:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 364:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 365:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 366:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 367:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 368:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 369:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 370:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 371:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 372:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 373:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 374:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 375:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 376:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 377:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 378:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 379:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 380:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 381:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 382:59 | [6 empty] | 0 | 0 | 0
2005-04-16 | 383:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 384:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 385:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 386:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 387:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 388:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 389:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 390:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 391:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 392:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 393:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 394:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 395:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 396:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 397:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 398:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 399:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 400:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 401:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 402:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 403:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 404:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 405:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 406:59 | [6 empty] | 0 | 0 | 0
2005-04-17 | 407:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 408:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 409:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 410:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 411:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 412:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 413:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 414:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 415:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 416:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 417:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 418:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 419:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 420:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 421:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 422:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 423:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 424:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 425:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 426:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 427:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 428:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 429:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 430:59 | [6 empty] | 0 | 0 | 0
2005-04-18 | 431:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 432:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 433:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 434:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 435:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 436:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 437:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 438:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 439:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 440:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 441:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 442:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 443:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 444:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 445:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 446:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 447:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 448:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 449:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 450:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 451:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 452:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 453:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 454:59 | [6 empty] | 0 | 0 | 0
2005-04-19 | 455:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 456:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 457:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 458:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 459:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 460:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 461:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 462:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 463:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 464:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 465:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 466:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 467:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 468:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 469:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 470:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 471:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 472:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 473:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 474:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 475:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 476:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 477:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 478:59 | [6 empty] | 0 | 0 | 0
2005-04-20 | 479:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 480:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 481:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 482:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 483:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 484:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 485:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 486:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 487:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 488:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 489:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 490:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 491:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 492:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 493:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 494:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 495:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 496:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 497:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 498:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 499:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 500:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 501:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 502:59 | [6 empty] | 0 | 0 | 0
2005-04-21 | 503:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 504:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 505:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 506:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 507:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 508:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 509:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 510:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 511:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 512:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 513:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 514:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 515:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 516:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 517:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 518:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 519:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 520:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 521:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 522:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 523:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 524:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 525:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 526:59 | [6 empty] | 0 | 0 | 0
2005-04-22 | 527:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 528:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 529:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 530:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 531:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 532:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 533:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 534:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 535:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 536:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 537:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 538:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 539:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 540:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 541:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 542:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 543:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 544:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 545:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 546:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 547:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 548:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 549:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 550:59 | [6 empty] | 0 | 0 | 0
2005-04-23 | 551:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 552:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 553:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 554:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 555:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 556:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 557:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 558:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 559:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 560:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 561:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 562:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 563:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 564:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 565:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 566:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 567:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 568:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 569:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 570:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 571:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 572:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 573:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 574:59 | [6 empty] | 0 | 0 | 0
2005-04-24 | 575:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 576:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 577:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 578:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 579:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 580:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 581:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 582:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 583:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 584:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 585:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 586:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 587:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 588:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 589:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 590:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 591:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 592:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 593:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 594:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 595:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 596:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 597:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 598:59 | [6 empty] | 0 | 0 | 0
2005-04-25 | 599:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 600:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 601:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 602:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 603:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 604:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 605:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 606:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 607:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 608:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 609:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 610:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 611:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 612:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 613:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 614:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 615:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 616:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 617:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 618:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 619:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 620:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 621:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 622:59 | [6 empty] | 0 | 0 | 0
2005-04-26 | 623:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 624:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 625:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 626:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 627:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 628:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 629:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 630:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 631:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 632:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 633:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 634:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 635:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 636:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 637:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 638:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 639:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 640:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 641:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 642:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 643:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 644:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 645:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 646:59 | [6 empty] | 0 | 0 | 0
2005-04-27 | 647:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 648:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 649:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 650:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 651:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 652:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 653:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 654:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 655:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 656:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 657:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 658:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 659:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 660:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 661:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 662:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 663:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 664:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 665:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 666:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 667:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 668:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 669:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 670:59 | [6 empty] | 0 | 0 | 0
2005-04-28 | 671:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 672:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 673:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 674:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 675:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 676:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 677:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 678:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 679:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 680:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 681:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 682:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 683:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 684:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 685:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 686:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 687:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 688:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 689:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 690:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 691:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 692:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 693:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 694:59 | [6 empty] | 0 | 0 | 0
2005-04-29 | 695:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 696:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 697:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 698:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 699:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 700:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 701:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 702:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 703:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 704:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 705:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 706:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 707:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 708:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 709:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 710:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 711:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 712:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 713:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 714:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 715:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 716:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 717:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 718:59 | [6 empty] | 0 | 0 | 0
2005-04-30 | 719:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 720:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 721:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 722:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 723:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 724:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 725:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 726:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 727:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 728:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 729:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 730:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 731:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 732:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 733:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 734:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 735:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 736:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 737:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 738:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 739:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 740:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 741:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 742:59 | [6 empty] | 0 | 0 | 0
2005-05-01 | 743:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 744:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 745:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 746:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 747:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 748:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 749:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 750:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 751:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 752:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 753:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 754:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 755:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 756:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 757:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 758:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 759:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 760:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 761:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 762:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 763:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 764:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 765:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 766:59 | [6 empty] | 0 | 0 | 0
2005-05-02 | 767:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 768:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 769:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 770:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 771:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 772:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 773:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 774:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 775:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 776:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 777:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 778:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 779:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 780:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 781:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 782:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 783:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 784:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 785:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 786:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 787:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 788:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 789:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 790:59 | [6 empty] | 0 | 0 | 0
2005-05-03 | 791:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 792:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 793:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 794:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 795:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 796:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 797:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 798:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 799:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 800:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 801:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 802:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 803:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 804:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 805:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 806:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 807:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 808:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 809:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 810:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 811:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 812:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 813:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 814:59 | [6 empty] | 0 | 0 | 0
2005-05-04 | 815:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 816:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 817:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 818:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 819:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 820:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 821:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 822:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 823:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 824:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 825:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 826:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 827:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 828:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 829:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 830:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 831:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 832:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 833:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 834:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 835:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 836:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 837:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 838:59 | [6 empty] | 0 | 0 | 0
2005-05-05 | 839:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 840:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 841:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 842:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 843:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 844:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 845:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 846:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 847:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 848:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 849:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 850:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 851:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 852:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 853:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 854:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 855:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 856:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 857:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 858:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 859:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 860:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 861:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 862:59 | [6 empty] | 0 | 0 | 0
2005-05-06 | 863:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 864:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 865:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 866:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 867:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 868:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 869:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 870:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 871:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 872:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 873:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 874:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 875:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 876:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 877:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 878:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 879:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 880:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 881:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 882:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 883:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 884:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 885:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 886:59 | [6 empty] | 0 | 0 | 0
2005-05-07 | 887:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 888:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 889:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 890:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 891:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 892:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 893:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 894:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 895:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 896:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 897:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 898:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 899:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 900:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 901:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 902:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 903:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 904:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 905:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 906:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 907:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 908:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 909:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 910:59 | [6 empty] | 0 | 0 | 0
2005-05-08 | 911:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 912:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 913:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 914:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 915:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 916:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 917:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 918:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 919:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 920:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 921:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 922:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 923:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 924:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 925:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 926:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 927:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 928:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 929:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 930:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 931:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 932:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 933:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 934:59 | [6 empty] | 0 | 0 | 0
2005-05-09 | 935:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 936:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 937:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 938:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 939:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 940:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 941:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 942:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 943:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 944:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 945:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 946:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 947:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 948:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 949:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 950:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 951:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 952:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 953:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 954:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 955:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 956:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 957:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 958:59 | [6 empty] | 0 | 0 | 0
2005-05-10 | 959:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 960:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 961:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 962:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 963:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 964:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 965:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 966:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 967:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 968:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 969:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 970:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 971:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 972:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 973:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 974:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 975:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 976:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 977:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 978:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 979:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 980:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 981:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 982:59 | [6 empty] | 0 | 0 | 0
2005-05-11 | 983:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 984:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 985:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 986:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 987:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 988:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 989:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 990:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 991:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 992:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 993:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 994:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 995:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 996:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 997:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 998:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 999:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 1000:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 1001:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 1002:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 1003:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 1004:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 1005:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 1006:59 | [6 empty] | 0 | 0 | 0
2005-05-12 | 1007:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1008:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1009:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1010:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1011:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1012:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1013:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1014:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1015:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1016:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1017:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1018:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1019:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1020:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1021:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1022:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1023:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1024:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1025:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1026:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1027:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1028:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1029:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1030:59 | [6 empty] | 0 | 0 | 0
2005-05-13 | 1031:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1032:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1033:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1034:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1035:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1036:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1037:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1038:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1039:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1040:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1041:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1042:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1043:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1044:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1045:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1046:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1047:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1048:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1049:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1050:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1051:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1052:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1053:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1054:59 | [6 empty] | 0 | 0 | 0
2005-05-14 | 1055:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1056:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1057:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1058:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1059:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1060:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1061:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1062:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1063:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1064:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1065:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1066:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1067:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1068:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1069:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1070:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1071:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1072:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1073:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1074:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1075:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1076:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1077:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1078:59 | [6 empty] | 0 | 0 | 0
2005-05-15 | 1079:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1080:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1081:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1082:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1083:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1084:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1085:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1086:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1087:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1088:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1089:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1090:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1091:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1092:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1093:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1094:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1095:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1096:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1097:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1098:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1099:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1100:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1101:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1102:59 | [6 empty] | 0 | 0 | 0
2005-05-16 | 1103:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1104:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1105:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1106:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1107:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1108:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1109:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1110:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1111:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1112:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1113:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1114:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1115:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1116:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1117:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1118:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1119:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1120:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1121:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1122:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1123:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1124:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1125:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1126:59 | [6 empty] | 0 | 0 | 0
2005-05-17 | 1127:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1128:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1129:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1130:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1131:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1132:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1133:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1134:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1135:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1136:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1137:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1138:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1139:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1140:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1141:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1142:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1143:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1144:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1145:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1146:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1147:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1148:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1149:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1150:59 | [6 empty] | 0 | 0 | 0
2005-05-18 | 1151:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1152:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1153:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1154:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1155:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1156:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1157:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1158:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1159:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1160:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1161:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1162:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1163:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1164:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1165:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1166:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1167:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1168:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1169:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1170:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1171:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1172:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1173:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1174:59 | [6 empty] | 0 | 0 | 0
2005-05-19 | 1175:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1176:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1177:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1178:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1179:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1180:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1181:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1182:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1183:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1184:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1185:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1186:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1187:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1188:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1189:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1190:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1191:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1192:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1193:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1194:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1195:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1196:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1197:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1198:59 | [6 empty] | 0 | 0 | 0
2005-05-20 | 1199:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1200:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1201:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1202:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1203:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1204:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1205:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1206:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1207:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1208:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1209:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1210:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1211:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1212:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1213:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1214:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1215:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1216:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1217:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1218:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1219:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1220:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1221:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1222:59 | [6 empty] | 0 | 0 | 0
2005-05-21 | 1223:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1224:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1225:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1226:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1227:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1228:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1229:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1230:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1231:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1232:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1233:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1234:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1235:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1236:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1237:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1238:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1239:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1240:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1241:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1242:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1243:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1244:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1245:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1246:59 | [6 empty] | 0 | 0 | 0
2005-05-22 | 1247:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1248:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1249:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1250:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1251:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1252:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1253:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1254:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1255:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1256:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1257:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1258:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1259:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1260:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1261:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1262:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1263:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1264:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1265:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1266:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1267:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1268:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1269:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1270:59 | [6 empty] | 0 | 0 | 0
2005-05-23 | 1271:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1272:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1273:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1274:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1275:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1276:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1277:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1278:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1279:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1280:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1281:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1282:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1283:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1284:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1285:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1286:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1287:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1288:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1289:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1290:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1291:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1292:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1293:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1294:59 | [6 empty] | 0 | 0 | 0
2005-05-24 | 1295:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1296:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1297:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1298:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1299:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1300:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1301:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1302:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1303:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1304:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1305:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1306:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1307:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1308:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1309:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1310:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1311:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1312:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1313:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1314:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1315:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1316:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1317:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1318:59 | [6 empty] | 0 | 0 | 0
2005-05-25 | 1319:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1320:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1321:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1322:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1323:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1324:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1325:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1326:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1327:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1328:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1329:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1330:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1331:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1332:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1333:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1334:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1335:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1336:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1337:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1338:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1339:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1340:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1341:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1342:59 | [6 empty] | 0 | 0 | 0
2005-05-26 | 1343:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1344:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1345:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1346:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1347:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1348:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1349:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1350:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1351:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1352:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1353:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1354:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1355:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1356:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1357:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1358:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1359:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1360:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1361:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1362:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1363:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1364:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1365:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1366:59 | [6 empty] | 0 | 0 | 0
2005-05-27 | 1367:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1368:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1369:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1370:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1371:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1372:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1373:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1374:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1375:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1376:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1377:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1378:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1379:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1380:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1381:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1382:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1383:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1384:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1385:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1386:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1387:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1388:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1389:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1390:59 | [6 empty] | 0 | 0 | 0
2005-05-28 | 1391:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1392:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1393:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1394:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1395:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1396:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1397:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1398:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1399:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1400:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1401:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1402:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1403:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1404:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1405:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1406:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1407:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1408:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1409:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1410:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1411:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1412:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1413:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1414:59 | [6 empty] | 0 | 0 | 0
2005-05-29 | 1415:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1416:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1417:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1418:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1419:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1420:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1421:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1422:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1423:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1424:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1425:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1426:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1427:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1428:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1429:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1430:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1431:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1432:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1433:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1434:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1435:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1436:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1437:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1438:59 | [6 empty] | 0 | 0 | 0
2005-05-30 | 1439:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1440:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1441:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1442:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1443:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1444:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1445:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1446:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1447:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1448:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1449:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1450:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1451:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1452:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1453:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1454:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1455:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1456:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1457:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1458:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1459:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1460:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1461:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1462:59 | [6 empty] | 0 | 0 | 0
2005-05-31 | 1463:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1464:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1465:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1466:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1467:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1468:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1469:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1470:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1471:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1472:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1473:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1474:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1475:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1476:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1477:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1478:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1479:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1480:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1481:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1482:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1483:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1484:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1485:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1486:59 | [6 empty] | 0 | 0 | 0
2005-06-01 | 1487:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1488:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1489:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1490:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1491:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1492:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1493:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1494:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1495:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1496:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1497:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1498:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1499:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1500:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1501:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1502:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1503:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1504:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1505:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1506:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1507:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1508:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1509:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1510:59 | [6 empty] | 0 | 0 | 0
2005-06-02 | 1511:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1512:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1513:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1514:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1515:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1516:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1517:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1518:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1519:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1520:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1521:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1522:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1523:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1524:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1525:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1526:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1527:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1528:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1529:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1530:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1531:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1532:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1533:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1534:59 | [6 empty] | 0 | 0 | 0
2005-06-03 | 1535:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1536:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1537:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1538:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1539:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1540:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1541:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1542:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1543:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1544:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1545:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1546:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1547:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1548:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1549:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1550:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1551:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1552:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1553:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1554:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1555:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1556:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1557:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1558:59 | [6 empty] | 0 | 0 | 0
2005-06-04 | 1559:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1560:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1561:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1562:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1563:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1564:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1565:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1566:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1567:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1568:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1569:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1570:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1571:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1572:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1573:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1574:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1575:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1576:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1577:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1578:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1579:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1580:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1581:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1582:59 | [6 empty] | 0 | 0 | 0
2005-06-05 | 1583:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1584:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1585:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1586:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1587:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1588:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1589:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1590:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1591:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1592:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1593:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1594:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1595:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1596:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1597:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1598:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1599:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1600:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1601:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1602:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1603:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1604:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1605:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1606:59 | [6 empty] | 0 | 0 | 0
2005-06-06 | 1607:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1608:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1609:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1610:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1611:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1612:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1613:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1614:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1615:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1616:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1617:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1618:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1619:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1620:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1621:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1622:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1623:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1624:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1625:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1626:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1627:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1628:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1629:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1630:59 | [6 empty] | 0 | 0 | 0
2005-06-07 | 1631:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1632:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1633:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1634:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1635:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1636:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1637:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1638:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1639:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1640:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1641:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1642:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1643:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1644:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1645:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1646:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1647:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1648:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1649:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1650:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1651:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1652:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1653:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1654:59 | [6 empty] | 0 | 0 | 0
2005-06-08 | 1655:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1656:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1657:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1658:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1659:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1660:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1661:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1662:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1663:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1664:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1665:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1666:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1667:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1668:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1669:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1670:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1671:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1672:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1673:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1674:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1675:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1676:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1677:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1678:59 | [6 empty] | 0 | 0 | 0
2005-06-09 | 1679:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1680:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1681:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1682:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1683:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1684:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1685:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1686:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1687:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1688:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1689:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1690:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1691:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1692:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1693:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1694:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1695:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1696:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1697:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1698:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1699:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1700:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1701:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1702:59 | [6 empty] | 0 | 0 | 0
2005-06-10 | 1703:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1704:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1705:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1706:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1707:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1708:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1709:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1710:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1711:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1712:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1713:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1714:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1715:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1716:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1717:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1718:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1719:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1720:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1721:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1722:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1723:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1724:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1725:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1726:59 | [6 empty] | 0 | 0 | 0
2005-06-11 | 1727:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1728:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1729:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1730:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1731:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1732:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1733:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1734:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1735:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1736:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1737:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1738:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1739:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1740:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1741:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1742:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1743:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1744:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1745:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1746:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1747:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1748:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1749:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1750:59 | [6 empty] | 0 | 0 | 0
2005-06-12 | 1751:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1752:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1753:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1754:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1755:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1756:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1757:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1758:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1759:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1760:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1761:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1762:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1763:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1764:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1765:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1766:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1767:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1768:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1769:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1770:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1771:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1772:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1773:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1774:59 | [6 empty] | 0 | 0 | 0
2005-06-13 | 1775:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1776:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1777:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1778:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1779:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1780:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1781:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1782:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1783:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1784:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1785:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1786:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1787:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1788:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1789:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1790:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1791:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1792:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1793:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1794:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1795:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1796:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1797:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1798:59 | [6 empty] | 0 | 0 | 0
2005-06-14 | 1799:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1800:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1801:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1802:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1803:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1804:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1805:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1806:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1807:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1808:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1809:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1810:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1811:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1812:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1813:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1814:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1815:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1816:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1817:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1818:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1819:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1820:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1821:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1822:59 | [6 empty] | 0 | 0 | 0
2005-06-15 | 1823:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1824:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1825:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1826:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1827:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1828:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1829:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1830:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1831:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1832:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1833:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1834:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1835:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1836:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1837:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1838:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1839:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1840:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1841:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1842:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1843:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1844:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1845:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1846:59 | [6 empty] | 0 | 0 | 0
2005-06-16 | 1847:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1848:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1849:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1850:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1851:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1852:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1853:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1854:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1855:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1856:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1857:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1858:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1859:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1860:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1861:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1862:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1863:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1864:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1865:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1866:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1867:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1868:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1869:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1870:59 | [6 empty] | 0 | 0 | 0
2005-06-17 | 1871:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1872:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1873:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1874:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1875:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1876:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1877:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1878:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1879:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1880:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1881:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1882:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1883:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1884:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1885:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1886:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1887:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1888:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1889:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1890:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1891:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1892:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1893:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1894:59 | [6 empty] | 0 | 0 | 0
2005-06-18 | 1895:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1896:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1897:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1898:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1899:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1900:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1901:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1902:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1903:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1904:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1905:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1906:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1907:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1908:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1909:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1910:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1911:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1912:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1913:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1914:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1915:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1916:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1917:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1918:59 | [6 empty] | 0 | 0 | 0
2005-06-19 | 1919:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1920:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1921:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1922:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1923:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1924:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1925:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1926:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1927:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1928:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1929:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1930:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1931:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1932:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1933:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1934:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1935:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1936:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1937:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1938:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1939:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1940:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1941:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1942:59 | [6 empty] | 0 | 0 | 0
2005-06-20 | 1943:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1944:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1945:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1946:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1947:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1948:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1949:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1950:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1951:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1952:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1953:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1954:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1955:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1956:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1957:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1958:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1959:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1960:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1961:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1962:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1963:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1964:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1965:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1966:59 | [6 empty] | 0 | 0 | 0
2005-06-21 | 1967:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1968:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1969:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1970:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1971:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1972:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1973:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1974:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1975:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1976:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1977:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1978:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1979:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1980:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1981:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1982:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1983:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1984:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1985:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1986:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1987:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1988:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1989:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1990:59 | [6 empty] | 0 | 0 | 0
2005-06-22 | 1991:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 1992:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 1993:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 1994:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 1995:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 1996:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 1997:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 1998:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 1999:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2000:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2001:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2002:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2003:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2004:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2005:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2006:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2007:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2008:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2009:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2010:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2011:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2012:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2013:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2014:59 | [6 empty] | 0 | 0 | 0
2005-06-23 | 2015:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2016:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2017:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2018:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2019:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2020:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2021:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2022:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2023:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2024:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2025:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2026:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2027:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2028:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2029:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2030:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2031:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2032:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2033:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2034:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2035:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2036:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2037:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2038:59 | [6 empty] | 0 | 0 | 0
2005-06-24 | 2039:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2040:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2041:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2042:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2043:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2044:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2045:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2046:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2047:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2048:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2049:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2050:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2051:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2052:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2053:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2054:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2055:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2056:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2057:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2058:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2059:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2060:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2061:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2062:59 | [6 empty] | 0 | 0 | 0
2005-06-25 | 2063:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2064:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2065:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2066:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2067:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2068:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2069:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2070:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2071:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2072:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2073:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2074:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2075:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2076:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2077:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2078:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2079:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2080:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2081:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2082:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2083:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2084:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2085:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2086:59 | [6 empty] | 0 | 0 | 0
2005-06-26 | 2087:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2088:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2089:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2090:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2091:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2092:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2093:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2094:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2095:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2096:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2097:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2098:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2099:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2100:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2101:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2102:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2103:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2104:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2105:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2106:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2107:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2108:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2109:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2110:59 | [6 empty] | 0 | 0 | 0
2005-06-27 | 2111:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2112:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2113:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2114:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2115:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2116:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2117:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2118:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2119:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2120:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2121:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2122:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2123:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2124:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2125:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2126:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2127:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2128:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2129:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2130:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2131:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2132:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2133:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2134:59 | [6 empty] | 0 | 0 | 0
2005-06-28 | 2135:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2136:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2137:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2138:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2139:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2140:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2141:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2142:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2143:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2144:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2145:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2146:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2147:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2148:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2149:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2150:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2151:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2152:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2153:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2154:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2155:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2156:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2157:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2158:59 | [6 empty] | 0 | 0 | 0
2005-06-29 | 2159:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2160:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2161:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2162:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2163:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2164:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2165:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2166:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2167:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2168:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2169:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2170:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2171:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2172:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2173:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2174:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2175:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2176:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2177:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2178:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2179:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2180:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2181:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2182:59 | [6 empty] | 0 | 0 | 0
2005-06-30 | 2183:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2184:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2185:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2186:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2187:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2188:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2189:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2190:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2191:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2192:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2193:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2194:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2195:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2196:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2197:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2198:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2199:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2200:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2201:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2202:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2203:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2204:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2205:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2206:59 | [6 empty] | 0 | 0 | 0
2005-07-01 | 2207:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2208:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2209:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2210:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2211:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2212:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2213:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2214:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2215:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2216:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2217:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2218:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2219:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2220:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2221:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2222:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2223:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2224:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2225:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2226:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2227:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2228:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2229:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2230:59 | [6 empty] | 0 | 0 | 0
2005-07-02 | 2231:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2232:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2233:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2234:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2235:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2236:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2237:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2238:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2239:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2240:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2241:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2242:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2243:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2244:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2245:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2246:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2247:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2248:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2249:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2250:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2251:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2252:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2253:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2254:59 | [6 empty] | 0 | 0 | 0
2005-07-03 | 2255:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2256:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2257:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2258:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2259:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2260:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2261:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2262:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2263:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2264:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2265:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2266:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2267:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2268:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2269:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2270:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2271:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2272:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2273:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2274:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2275:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2276:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2277:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2278:59 | [6 empty] | 0 | 0 | 0
2005-07-04 | 2279:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2280:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2281:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2282:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2283:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2284:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2285:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2286:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2287:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2288:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2289:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2290:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2291:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2292:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2293:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2294:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2295:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2296:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2297:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2298:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2299:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2300:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2301:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2302:59 | [6 empty] | 0 | 0 | 0
2005-07-05 | 2303:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2304:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2305:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2306:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2307:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2308:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2309:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2310:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2311:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2312:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2313:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2314:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2315:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2316:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2317:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2318:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2319:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2320:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2321:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2322:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2323:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2324:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2325:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2326:59 | [6 empty] | 0 | 0 | 0
2005-07-06 | 2327:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2328:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2329:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2330:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2331:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2332:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2333:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2334:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2335:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2336:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2337:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2338:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2339:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2340:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2341:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2342:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2343:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2344:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2345:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2346:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2347:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2348:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2349:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2350:59 | [6 empty] | 0 | 0 | 0
2005-07-07 | 2351:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2352:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2353:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2354:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2355:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2356:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2357:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2358:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2359:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2360:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2361:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2362:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2363:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2364:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2365:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2366:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2367:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2368:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2369:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2370:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2371:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2372:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2373:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2374:59 | [6 empty] | 0 | 0 | 0
2005-07-08 | 2375:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2376:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2377:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2378:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2379:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2380:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2381:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2382:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2383:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2384:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2385:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2386:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2387:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2388:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2389:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2390:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2391:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2392:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2393:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2394:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2395:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2396:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2397:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2398:59 | [6 empty] | 0 | 0 | 0
2005-07-09 | 2399:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2400:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2401:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2402:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2403:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2404:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2405:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2406:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2407:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2408:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2409:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2410:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2411:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2412:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2413:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2414:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2415:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2416:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2417:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2418:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2419:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2420:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2421:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2422:59 | [6 empty] | 0 | 0 | 0
2005-07-10 | 2423:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2424:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2425:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2426:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2427:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2428:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2429:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2430:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2431:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2432:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2433:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2434:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2435:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2436:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2437:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2438:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2439:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2440:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2441:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2442:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2443:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2444:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2445:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2446:59 | [6 empty] | 0 | 0 | 0
2005-07-11 | 2447:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2448:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2449:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2450:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2451:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2452:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2453:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2454:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2455:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2456:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2457:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2458:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2459:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2460:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2461:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2462:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2463:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2464:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2465:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2466:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2467:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2468:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2469:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2470:59 | [6 empty] | 0 | 0 | 0
2005-07-12 | 2471:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2472:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2473:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2474:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2475:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2476:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2477:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2478:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2479:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2480:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2481:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2482:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2483:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2484:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2485:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2486:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2487:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2488:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2489:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2490:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2491:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2492:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2493:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2494:59 | [6 empty] | 0 | 0 | 0
2005-07-13 | 2495:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2496:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2497:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2498:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2499:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2500:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2501:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2502:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2503:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2504:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2505:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2506:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2507:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2508:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2509:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2510:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2511:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2512:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2513:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2514:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2515:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2516:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2517:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2518:59 | [6 empty] | 0 | 0 | 0
2005-07-14 | 2519:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2520:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2521:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2522:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2523:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2524:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2525:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2526:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2527:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2528:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2529:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2530:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2531:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2532:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2533:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2534:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2535:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2536:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2537:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2538:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2539:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2540:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2541:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2542:59 | [6 empty] | 0 | 0 | 0
2005-07-15 | 2543:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2544:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2545:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2546:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2547:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2548:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2549:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2550:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2551:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2552:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2553:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2554:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2555:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2556:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2557:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2558:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2559:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2560:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2561:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2562:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2563:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2564:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2565:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2566:59 | [6 empty] | 0 | 0 | 0
2005-07-16 | 2567:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2568:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2569:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2570:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2571:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2572:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2573:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2574:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2575:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2576:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2577:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2578:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2579:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2580:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2581:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2582:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2583:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2584:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2585:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2586:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2587:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2588:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2589:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2590:59 | [6 empty] | 0 | 0 | 0
2005-07-17 | 2591:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2592:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2593:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2594:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2595:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2596:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2597:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2598:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2599:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2600:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2601:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2602:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2603:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2604:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2605:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2606:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2607:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2608:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2609:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2610:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2611:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2612:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2613:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2614:59 | [6 empty] | 0 | 0 | 0
2005-07-18 | 2615:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2616:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2617:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2618:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2619:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2620:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2621:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2622:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2623:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2624:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2625:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2626:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2627:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2628:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2629:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2630:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2631:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2632:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2633:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2634:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2635:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2636:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2637:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2638:59 | [6 empty] | 0 | 0 | 0
2005-07-19 | 2639:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2640:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2641:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2642:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2643:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2644:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2645:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2646:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2647:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2648:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2649:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2650:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2651:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2652:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2653:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2654:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2655:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2656:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2657:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2658:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2659:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2660:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2661:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2662:59 | [6 empty] | 0 | 0 | 0
2005-07-20 | 2663:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2664:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2665:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2666:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2667:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2668:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2669:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2670:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2671:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2672:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2673:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2674:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2675:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2676:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2677:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2678:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2679:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2680:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2681:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2682:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2683:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2684:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2685:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2686:59 | [6 empty] | 0 | 0 | 0
2005-07-21 | 2687:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2688:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2689:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2690:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2691:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2692:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2693:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2694:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2695:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2696:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2697:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2698:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2699:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2700:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2701:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2702:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2703:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2704:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2705:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2706:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2707:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2708:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2709:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2710:59 | [6 empty] | 0 | 0 | 0
2005-07-22 | 2711:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2712:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2713:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2714:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2715:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2716:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2717:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2718:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2719:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2720:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2721:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2722:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2723:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2724:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2725:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2726:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2727:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2728:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2729:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2730:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2731:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2732:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2733:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2734:59 | [6 empty] | 0 | 0 | 0
2005-07-23 | 2735:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2736:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2737:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2738:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2739:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2740:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2741:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2742:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2743:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2744:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2745:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2746:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2747:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2748:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2749:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2750:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2751:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2752:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2753:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2754:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2755:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2756:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2757:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2758:59 | [6 empty] | 0 | 0 | 0
2005-07-24 | 2759:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2760:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2761:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2762:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2763:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2764:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2765:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2766:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2767:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2768:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2769:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2770:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2771:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2772:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2773:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2774:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2775:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2776:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2777:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2778:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2779:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2780:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2781:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2782:59 | [6 empty] | 0 | 0 | 0
2005-07-25 | 2783:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2784:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2785:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2786:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2787:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2788:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2789:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2790:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2791:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2792:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2793:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2794:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2795:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2796:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2797:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2798:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2799:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2800:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2801:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2802:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2803:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2804:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2805:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2806:59 | [6 empty] | 0 | 0 | 0
2005-07-26 | 2807:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2808:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2809:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2810:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2811:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2812:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2813:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2814:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2815:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2816:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2817:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2818:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2819:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2820:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2821:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2822:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2823:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2824:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2825:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2826:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2827:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2828:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2829:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2830:59 | [6 empty] | 0 | 0 | 0
2005-07-27 | 2831:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2832:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2833:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2834:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2835:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2836:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2837:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2838:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2839:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2840:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2841:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2842:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2843:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2844:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2845:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2846:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2847:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2848:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2849:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2850:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2851:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2852:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2853:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2854:59 | [6 empty] | 0 | 0 | 0
2005-07-28 | 2855:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2856:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2857:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2858:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2859:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2860:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2861:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2862:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2863:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2864:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2865:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2866:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2867:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2868:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2869:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2870:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2871:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2872:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2873:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2874:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2875:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2876:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2877:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2878:59 | [6 empty] | 0 | 0 | 0
2005-07-29 | 2879:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2880:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2881:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2882:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2883:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2884:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2885:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2886:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2887:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2888:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2889:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2890:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2891:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2892:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2893:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2894:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2895:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2896:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2897:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2898:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2899:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2900:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2901:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2902:59 | [6 empty] | 0 | 0 | 0
2005-08-01 | 2903:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2904:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2905:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2906:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2907:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2908:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2909:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2910:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2911:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2912:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2913:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2914:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2915:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2916:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2917:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2918:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2919:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2920:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2921:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2922:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2923:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2924:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2925:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2926:59 | [6 empty] | 0 | 0 | 0
2005-08-02 | 2927:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2928:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2929:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2930:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2931:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2932:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2933:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2934:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2935:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2936:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2937:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2938:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2939:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2940:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2941:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2942:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2943:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2944:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2945:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2946:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2947:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2948:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2949:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2950:59 | [6 empty] | 0 | 0 | 0
2005-08-03 | 2951:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2952:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2953:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2954:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2955:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2956:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2957:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2958:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2959:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2960:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2961:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2962:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2963:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2964:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2965:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2966:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2967:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2968:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2969:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2970:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2971:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2972:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2973:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2974:59 | [6 empty] | 0 | 0 | 0
2005-08-04 | 2975:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2976:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2977:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2978:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2979:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2980:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2981:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2982:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2983:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2984:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2985:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2986:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2987:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2988:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2989:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2990:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2991:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2992:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2993:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2994:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2995:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2996:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2997:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2998:59 | [6 empty] | 0 | 0 | 0
2005-08-05 | 2999:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3000:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3001:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3002:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3003:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3004:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3005:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3006:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3007:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3008:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3009:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3010:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3011:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3012:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3013:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3014:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3015:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3016:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3017:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3018:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3019:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3020:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3021:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3022:59 | [6 empty] | 0 | 0 | 0
2005-08-06 | 3023:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3024:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3025:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3026:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3027:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3028:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3029:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3030:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3031:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3032:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3033:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3034:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3035:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3036:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3037:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3038:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3039:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3040:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3041:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3042:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3043:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3044:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3045:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3046:59 | [6 empty] | 0 | 0 | 0
2005-08-07 | 3047:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3048:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3049:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3050:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3051:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3052:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3053:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3054:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3055:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3056:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3057:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3058:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3059:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3060:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3061:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3062:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3063:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3064:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3065:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3066:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3067:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3068:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3069:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3070:59 | [6 empty] | 0 | 0 | 0
2005-08-08 | 3071:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3072:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3073:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3074:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3075:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3076:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3077:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3078:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3079:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3080:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3081:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3082:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3083:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3084:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3085:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3086:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3087:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3088:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3089:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3090:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3091:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3092:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3093:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3094:59 | [6 empty] | 0 | 0 | 0
2005-08-09 | 3095:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3096:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3097:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3098:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3099:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3100:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3101:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3102:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3103:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3104:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3105:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3106:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3107:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3108:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3109:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3110:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3111:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3112:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3113:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3114:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3115:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3116:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3117:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3118:59 | [6 empty] | 0 | 0 | 0
2005-08-10 | 3119:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3120:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3121:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3122:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3123:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3124:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3125:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3126:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3127:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3128:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3129:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3130:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3131:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3132:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3133:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3134:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3135:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3136:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3137:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3138:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3139:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3140:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3141:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3142:59 | [6 empty] | 0 | 0 | 0
2005-08-11 | 3143:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3144:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3145:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3146:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3147:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3148:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3149:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3150:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3151:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3152:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3153:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3154:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3155:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3156:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3157:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3158:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3159:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3160:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3161:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3162:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3163:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3164:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3165:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3166:59 | [6 empty] | 0 | 0 | 0
2005-08-12 | 3167:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3168:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3169:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3170:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3171:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3172:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3173:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3174:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3175:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3176:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3177:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3178:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3179:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3180:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3181:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3182:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3183:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3184:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3185:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3186:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3187:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3188:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3189:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3190:59 | [6 empty] | 0 | 0 | 0
2005-08-13 | 3191:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3192:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3193:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3194:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3195:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3196:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3197:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3198:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3199:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3200:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3201:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3202:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3203:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3204:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3205:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3206:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3207:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3208:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3209:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3210:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3211:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3212:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3213:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3214:59 | [6 empty] | 0 | 0 | 0
2005-08-14 | 3215:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3216:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3217:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3218:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3219:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3220:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3221:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3222:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3223:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3224:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3225:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3226:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3227:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3228:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3229:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3230:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3231:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3232:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3233:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3234:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3235:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3236:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3237:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3238:59 | [6 empty] | 0 | 0 | 0
2005-08-15 | 3239:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3240:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3241:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3242:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3243:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3244:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3245:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3246:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3247:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3248:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3249:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3250:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3251:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3252:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3253:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3254:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3255:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3256:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3257:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3258:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3259:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3260:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3261:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3262:59 | [6 empty] | 0 | 0 | 0
2005-08-16 | 3263:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3264:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3265:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3266:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3267:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3268:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3269:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3270:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3271:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3272:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3273:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3274:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3275:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3276:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3277:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3278:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3279:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3280:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3281:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3282:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3283:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3284:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3285:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3286:59 | [6 empty] | 0 | 0 | 0
2005-08-17 | 3287:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3288:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3289:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3290:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3291:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3292:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3293:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3294:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3295:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3296:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3297:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3298:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3299:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3300:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3301:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3302:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3303:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3304:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3305:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3306:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3307:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3308:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3309:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3310:59 | [6 empty] | 0 | 0 | 0
2005-08-18 | 3311:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3312:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3313:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3314:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3315:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3316:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3317:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3318:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3319:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3320:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3321:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3322:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3323:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3324:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3325:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3326:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3327:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3328:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3329:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3330:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3331:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3332:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3333:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3334:59 | [6 empty] | 0 | 0 | 0
2005-08-19 | 3335:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3336:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3337:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3338:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3339:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3340:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3341:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3342:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3343:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3344:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3345:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3346:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3347:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3348:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3349:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3350:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3351:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3352:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3353:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3354:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3355:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3356:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3357:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3358:59 | [6 empty] | 0 | 0 | 0
2005-08-20 | 3359:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3360:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3361:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3362:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3363:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3364:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3365:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3366:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3367:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3368:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3369:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3370:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3371:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3372:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3373:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3374:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3375:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3376:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3377:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3378:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3379:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3380:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3381:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3382:59 | [6 empty] | 0 | 0 | 0
2005-08-21 | 3383:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3384:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3385:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3386:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3387:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3388:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3389:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3390:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3391:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3392:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3393:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3394:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3395:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3396:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3397:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3398:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3399:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3400:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3401:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3402:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3403:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3404:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3405:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3406:59 | [6 empty] | 0 | 0 | 0
2005-08-22 | 3407:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3408:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3409:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3410:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3411:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3412:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3413:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3414:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3415:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3416:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3417:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3418:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3419:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3420:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3421:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3422:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3423:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3424:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3425:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3426:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3427:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3428:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3429:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3430:59 | [6 empty] | 0 | 0 | 0
2005-08-23 | 3431:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3432:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3433:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3434:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3435:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3436:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3437:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3438:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3439:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3440:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3441:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3442:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3443:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3444:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3445:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3446:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3447:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3448:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3449:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3450:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3451:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3452:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3453:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3454:59 | [6 empty] | 0 | 0 | 0
2005-08-24 | 3455:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3456:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3457:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3458:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3459:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3460:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3461:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3462:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3463:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3464:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3465:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3466:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3467:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3468:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3469:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3470:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3471:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3472:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3473:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3474:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3475:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3476:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3477:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3478:59 | [6 empty] | 0 | 0 | 0
2005-08-25 | 3479:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3480:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3481:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3482:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3483:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3484:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3485:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3486:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3487:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3488:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3489:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3490:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3491:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3492:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3493:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3494:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3495:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3496:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3497:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3498:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3499:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3500:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3501:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3502:59 | [6 empty] | 0 | 0 | 0
2005-08-26 | 3503:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3504:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3505:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3506:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3507:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3508:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3509:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3510:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3511:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3512:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3513:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3514:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3515:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3516:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3517:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3518:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3519:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3520:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3521:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3522:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3523:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3524:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3525:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3526:59 | [6 empty] | 0 | 0 | 0
2005-08-27 | 3527:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3528:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3529:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3530:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3531:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3532:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3533:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3534:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3535:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3536:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3537:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3538:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3539:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3540:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3541:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3542:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3543:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3544:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3545:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3546:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3547:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3548:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3549:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3550:59 | [6 empty] | 0 | 0 | 0
2005-08-28 | 3551:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3552:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3553:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3554:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3555:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3556:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3557:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3558:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3559:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3560:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3561:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3562:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3563:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3564:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3565:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3566:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3567:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3568:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3569:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3570:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3571:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3572:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3573:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3574:59 | [6 empty] | 0 | 0 | 0
2005-08-29 | 3575:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3576:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3577:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3578:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3579:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3580:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3581:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3582:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3583:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3584:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3585:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3586:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3587:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3588:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3589:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3590:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3591:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3592:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3593:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3594:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3595:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3596:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3597:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3598:59 | [6 empty] | 0 | 0 | 0
2005-08-30 | 3599:59 | [6 empty] | 0 | 0 | 0
2005-08-31 | 3600:59 | [6 empty] | 0 | 0 | 0
2005-08-31 | 3601:59 | [6 empty] | 0 | 0 | 0
2005-09-01 | 0:59 | 47 | 13.1 | -61.2 | 37 | 0 | 674.4 | 0 | -61.2 | 0
2005-09-01 | 1:59 | 37 | 12.8 | -60.7 | 38 | 0 | 674.2 | 0 | -60.7 | 0
2005-09-01 | 2:59 | 51 | 11 | -61.7 | 37 | 0 | 673.9 | 0 | -61.7 | 0
2005-09-01 | 3:59 | 38 | 14.7 | -60.9 | 38 | 0 | 673.6 | 0 | -60.9 | 0
2005-09-01 | 4:59 | 41 | 13.6 | -61 | 37 | 0 | 673.4 | 0 | -61 | 0
2005-09-01 | 5:59 | 33 | 14 | -60.2 | 38 | 0 | 673.1 | 0 | -60.2 | 0
2005-09-01 | 6:59 | 41 | 12.9 | -59.8 | 39 | 0 | 672.7 | 0 | -59.8 | 0
2005-09-01 | 7:59 | 45 | 13.4 | -58.6 | 40 | 0 | 672.3 | 0 | -58.6 | 0
2005-09-01 | 8:59 | 40 | 13 | -59.1 | 39 | 0 | 672 | 0 | -59.1 | 0
2005-09-01 | 9:59 | 42 | 12.6 | -60.1 | 38 | 0 | 671.6 | 0 | -60.1 | 0
2005-09-01 | 10:59 | 47 | 14.8 | -58.6 | 40 | 0 | 671.3 | 0 | -58.6 | 0
2005-09-01 | 11:59 | 43 | 14 | -58.4 | 40 | 0 | 670.9 | 0 | -58.4 | 0
2005-09-01 | 12:59 | 47 | 12.9 | -57.9 | 41 | 0 | 670.4 | 0 | -57.9 | 0
2005-09-01 | 13:59 | 48 | 13 | -58.5 | 40 | 0 | 670.1 | 0 | -58.5 | 0
2005-09-01 | 14:59 | 39 | 17.6 | -56.8 | 42 | 0 | 669.8 | 0 | -56.8 | 0
2005-09-01 | 15:59 | 41 | 15.3 | -56.9 | 42 | 0 | 669.2 | 0 | -56.9 | 0
2005-09-01 | 16:59 | 35 | 19.9 | -56 | 43 | 0 | 668.7 | 0 | -56 | 0
2005-09-01 | 17:59 | 32 | 16.8 | -55.8 | 43 | 0 | 668.2 | 0 | -55.8 | 0
2005-09-01 | 18:59 | 35 | 16.9 | -56.3 | 43 | 0 | 667.9 | 0 | -56.3 | 0
2005-09-01 | 19:59 | 35 | 16.5 | -55.7 | 43 | 0 | 667.7 | 0 | -55.7 | 0
2005-09-01 | 20:59 | 25 | 18 | -55.2 | 44 | 0 | 667.4 | 0 | -55.2 | 0
2005-09-01 | 21:59 | 25 | 20.4 | -54.2 | 45 | 0 | 667.1 | 0 | -54.2 | 0
2005-09-01 | 22:59 | 24 | 17.8 | -54.2 | 45 | 0 | 666.8 | 0 | -54.2 | 0
2005-09-01 | 23:59 | 18 | 18.4 | -54 | 45 | 0 | 666.5 | 0 | -54 | 0
2005-09-02 | 0:59 | 20 | 17.6 | -54.6 | 45 | 0 | 666.4 | 0 | -54.6 | 0
2005-09-02 | 1:59 | 18 | 18.6 | -55.7 | 44 | 0 | 666.2 | 0 | -55.7 | 0
2005-09-02 | 2:59 | 23 | 19.7 | -55.9 | 43 | 0 | 666.1 | 0 | -55.9 | 0
2005-09-02 | 3:59 | 22 | 21.5 | -55.7 | 44 | 0 | 665.9 | 0 | -55.7 | 0
2005-09-02 | 4:59 | 14 | 17.5 | -56.7 | 42 | 0 | 665.9 | 0 | -56.7 | 0
2005-09-02 | 5:59 | 15 | 18.8 | -57.3 | 42 | 0 | 666.1 | 0 | -57.3 | 0
2005-09-02 | 6:59 | 21 | 18.3 | -57 | 42 | 0 | 666.2 | 0 | -57 | 0
2005-09-02 | 7:59 | 19 | 16.2 | -56.9 | 42 | 0 | 666.5 | 0 | -56.9 | 0
2005-09-02 | 8:59 | 19 | 15.9 | -57.2 | 42 | 0 | 666.7 | 0 | -57.2 | 0
2005-09-02 | 9:59 | 21 | 16.2 | -57.6 | 41 | 0 | 666.8 | 0 | -57.6 | 0
2005-09-02 | 10:59 | 22 | 20.3 | -58 | 41 | 0 | 666.8 | 0 | -58 | 0
2005-09-02 | 11:59 | 16 | 19.2 | -58 | 41 | 0 | 666.9 | 0 | -58 | 0
2005-09-02 | 12:59 | 26 | 18.5 | -58.3 | 41 | 0 | 667.4 | 0 | -58.3 | 0
2005-09-02 | 13:59 | 21 | 19.2 | -58.8 | 40 | 0 | 667.6 | 0 | -58.8 | 0
2005-09-02 | 14:59 | 24 | 18.2 | -58.8 | 40 | 0 | 668.1 | 0 | -58.8 | 0
2005-09-02 | 15:59 | 13 | 21.1 | -58.4 | 41 | 0 | 667.9 | 0 | -58.4 | 0
2005-09-02 | 16:59 | 12 | 21.8 | -59.1 | 40 | 0 | 668.2 | 0 | -59.1 | 0
2005-09-02 | 17:59 | 13 | 21.8 | -58.8 | 40 | 0 | 668.7 | 0 | -58.8 | 0
2005-09-02 | 18:59 | 17 | 18.3 | -59 | 40 | 0 | 669.2 | 0 | -59 | 0
2005-09-02 | 19:59 | 5 | 19.2 | -58.7 | 40 | 0 | 669.6 | 0 | -58.7 | 0
2005-09-02 | 20:59 | 6 | 20.2 | -58.9 | 40 | 0 | 669.8 | 0 | -58.9 | 0
2005-09-02 | 21:59 | 11 | 19.4 | -59.3 | 39 | 0 | 670.5 | 0 | -59.3 | 0
2005-09-02 | 22:59 | 4 | 20.3 | -59.1 | 40 | 0 | 670.4 | 0 | -59.1 | 0
2005-09-02 | 23:59 | 6 | 21.7 | -58.5 | 40 | 0 | 670.8 | 0 | -58.5 | 0
2005-09-03 | 0:59 | 2 | 21.8 | -58.2 | 41 | 0 | 671.5 | 0 | -58.2 | 0
2005-09-03 | 1:59 | 4 | 22 | -57.6 | 41 | 0 | 671.7 | 0 | -57.6 | 0
2005-09-03 | 2:59 | 1 | 21 | -56.8 | 42 | 0 | 672.5 | 0 | -56.8 | 0
2005-09-03 | 3:59 | 356 | 19 | -56.2 | 43 | 0 | 672.9 | 0 | -56.2 | 0
2005-09-03 | 4:59 | 4 | 19.4 | -56 | 43 | 0 | 673.5 | 0 | -56 | 0
2005-09-03 | 5:59 | 0 | 19.8 | -55.8 | 43 | 0 | 673.9 | 0 | -55.8 | 0
2005-09-03 | 6:59 | 5 | 14.4 | -55.4 | 43 | 0 | 674.5 | 0 | -55.4 | 0
2005-09-03 | 7:59 | 10 | 15.9 | -55 | 44 | 0 | 675.1 | 0 | -55 | 0
2005-09-03 | 8:59 | 6 | 18.4 | -54.2 | 45 | 0 | 675.4 | 0 | -54.2 | 0
2005-09-03 | 9:59 | 0 | 20.2 | -53.2 | 46 | 0 | 675.7 | 0 | -53.2 | 0
2005-09-03 | 10:59 | 357 | 17.2 | -52.8 | 46 | 0 | 675.8 | 0 | -52.8 | 0
2005-09-03 | 11:59 | 1 | 22.1 | -52.5 | 47 | 0 | 675.9 | 0 | -52.5 | 0
2005-09-03 | 12:59 | 49 | 11.7 | -52 | 47 | 0 | 676.4 | 0 | -52 | 0
2005-09-03 | 13:59 | 1 | 16.8 | -52 | 48 | 0 | 676.8 | 0 | -52 | 0
2005-09-03 | 14:59 | 3 | 18.2 | -52 | 48 | 0 | 676.9 | 0 | -52 | 0
2005-09-03 | 15:59 | 0 | 21.4 | -51.3 | 48 | 0 | 676.9 | 0 | -51.3 | 0
2005-09-03 | 16:59 | 348 | 24.5 | -50.2 | 49 | 0 | 677 | 0 | -50.2 | 0
2005-09-03 | 17:59 | 4 | 20.5 | -50 | 50 | 0 | 677.7 | 0 | -50 | 0
2005-09-03 | 18:59 | 354 | 18.7 | -50 | 50 | 0 | 677.9 | 0 | -50 | 0
2005-09-03 | 19:59 | 350 | 20.3 | -49.3 | 51 | 0 | 678.1 | 0 | -49.3 | 0
2005-09-03 | 20:59 | 356 | 22.9 | -50.2 | 50 | 0 | 678.4 | 0 | -50.2 | 0
2005-09-03 | 21:59 | 353 | 21.5 | -50.2 | 50 | 0 | 678.3 | 0 | -50.2 | 0
2005-09-03 | 22:59 | 358 | 24.6 | -49.2 | 51 | 0 | 678.2 | 0 | -49.2 | 0
2005-09-03 | 23:59 | 345 | 19.8 | -48.8 | 51 | 0 | 678.3 | 0 | -48.8 | 0
2005-09-04 | 0:59 | 357 | 19.6 | -48.9 | 51 | 0 | 678.2 | 0 | -48.9 | 0
2005-09-04 | 1:59 | 9 | 16.6 | -48.8 | 51 | 0 | 678.2 | 0 | -48.8 | 0
2005-09-04 | 2:59 | 0 | 20 | -48.6 | 52 | 0 | 678.1 | 0 | -48.6 | 0
2005-09-04 | 3:59 | 353 | 23.5 | -47.7 | 53 | 0 | 677.9 | 0 | -47.7 | 0
2005-09-04 | 4:59 | 348 | 22.2 | -47.4 | 53 | 0 | 677.9 | 0 | -47.4 | 0
2005-09-04 | 5:59 | 344 | 17 | -46.3 | 54 | 0 | 677.8 | 0 | -46.3 | 0
2005-09-04 | 6:59 | 331 | 18.8 | -45.5 | 55 | 0 | 677.9 | 0 | -45.5 | 0
2005-09-04 | 7:59 | 322 | 17.5 | -45.3 | 55 | 0 | 678.2 | 0 | -45.3 | 0
2005-09-04 | 8:59 | 324 | 12.9 | -45.8 | 55 | 0 | 678.9 | 0 | -45.8 | 0
2005-09-04 | 9:59 | 329 | 14.3 | -46.2 | 54 | 0 | 679.1 | 0 | -46.2 | 0
2005-09-04 | 10:59 | 324 | 14.7 | -47.3 | 54 | 0 | 679.2 | 0 | -47.3 | 0
2005-09-04 | 11:59 | 330 | 10.9 | -47.8 | 53 | 0 | 679.3 | 0 | -47.8 | 0
2005-09-04 | 12:59 | 346 | 12.9 | -49.4 | 52 | 0 | 679.7 | 0 | -49.4 | 0
2005-09-04 | 13:59 | 351 | 12.5 | -48.2 | 52 | 0 | 679.7 | 0 | -48.2 | 0
2005-09-04 | 14:59 | 350 | 16 | -47 | 54 | 0 | 679.6 | 0 | -47 | 0
2005-09-04 | 15:59 | 332 | 16.8 | -45.9 | 55 | 0 | 679.5 | 0 | -45.9 | 0
2005-09-04 | 16:59 | 340 | 17.5 | -44.6 | 56 | 0 | 679.1 | 0 | -44.6 | 0
2005-09-04 | 17:59 | 328 | 24.2 | -43.6 | 57 | 0 | 678.4 | 0 | -43.6 | 0
2005-09-04 | 18:59 | 327 | 20.2 | -43.4 | 57 | 0 | 678.6 | 0 | -43.4 | 0
2005-09-04 | 19:59 | 318 | 26.6 | -42.5 | 58 | 0 | 678.1 | 0 | -42.5 | 0
2005-09-04 | 20:59 | 319 | 29.1 | -41.2 | 59 | 0 | 677.9 | 0 | -41.2 | 0
2005-09-04 | 21:59 | 306 | 24.9 | -40.9 | 60 | 0 | 677.8 | 0 | -40.9 | 0
2005-09-04 | 22:59 | 318 | 24.5 | -41.2 | 59 | 0 | 677.6 | 0 | -41.2 | 0
2005-09-04 | 23:59 | 305 | 28.5 | -40.4 | 60 | 0 | 677.8 | 0 | -40.4 | 0
2005-09-05 | 0:59 | 306 | 30.1 | -40.7 | 60 | 0 | 678 | 0 | -40.7 | 0
2005-09-05 | 1:59 | 311 | 28.9 | -41.2 | 60 | 0 | 678.3 | 0 | -41.2 | 0
2005-09-05 | 2:59 | 312 | 25 | -40.3 | 60 | 0 | 678.5 | 0 | -40.3 | 0
2005-09-05 | 3:59 | 313 | 20.3 | -40.2 | 61 | 0 | 678.8 | 0 | -40.2 | 0
2005-09-05 | 4:59 | 314 | 22.2 | -40.4 | 60 | 0 | 678.6 | 0 | -40.4 | 0
2005-09-05 | 5:59 | 321 | 20.5 | -39.9 | 61 | 0 | 679.2 | 0 | -39.9 | 0
2005-09-05 | 6:59 | 319 | 18.4 | -39.7 | 61 | 0 | 679.5 | 0 | -39.7 | 0
2005-09-05 | 7:59 | 307 | 27 | -39.8 | 61 | 0 | 679.1 | 0 | -39.8 | 0
2005-09-05 | 8:59 | 305 | 28.4 | -40.2 | 61 | 0 | 679.2 | 0 | -40.2 | 0
2005-09-05 | 9:59 | 311 | 14.9 | -41.1 | 60 | 0 | 679.9 | 0 | -41.1 | 0
2005-09-05 | 10:59 | 337 | 13.4 | -41.4 | 60 | 0 | 680.5 | 0 | -41.4 | 0
2005-09-05 | 11:59 | 334 | 13.5 | -41.5 | 60 | 0 | 680.6 | 0 | -41.5 | 0
2005-09-05 | 12:59 | 321 | 16.8 | -41.3 | 60 | 0 | 680.7 | 0 | -41.3 | 0
2005-09-05 | 13:59 | 317 | 15.6 | -41.9 | 59 | 0 | 680.9 | 0 | -41.9 | 0
2005-09-05 | 14:59 | 318 | 15 | -42.7 | 59 | 0 | 680.9 | 0 | -42.7 | 0
2005-09-05 | 15:59 | 305 | 12.6 | -43.1 | 58 | 0 | 681 | 0 | -43.1 | 0
2005-09-05 | 16:59 | 319 | 5.8 | -45.2 | 56 | 0 | 681.8 | 0 | -45.2 | 0
2005-09-05 | 17:59 | 324 | 9.6 | -45.4 | 56 | 0 | 682 | 0 | -45.4 | 0
2005-09-05 | 18:59 | 320 | 9 | -45.7 | 56 | 0 | 681.9 | 0 | -45.7 | 0
2005-09-05 | 19:59 | 325 | 10 | -45.3 | 56 | 0 | 682.1 | 0 | -45.3 | 0
2005-09-05 | 20:59 | 337 | 8.7 | -46.3 | 55 | 0 | 682.6 | 0 | -46.3 | 0
2005-09-05 | 21:59 | 325 | 11.4 | -45.8 | 55 | 0 | 682.6 | 0 | -45.8 | 0
2005-09-05 | 22:59 | 324 | 8.4 | -45.8 | 55 | 0 | 683.1 | 0 | -45.8 | 0
2005-09-05 | 23:59 | 311 | 11 | -45.5 | 56 | 0 | 683.4 | 0 | -45.5 | 0
2005-09-06 | 0:59 | 315 | 10.5 | -46 | 55 | 0 | 683.7 | 0 | -46 | 0
2005-09-06 | 1:59 | 316 | 10.3 | -46.4 | 55 | 0 | 683.9 | 0 | -46.4 | 0
2005-09-06 | 2:59 | 310 | 13.8 | -46 | 55 | 0 | 684.2 | 0 | -46 | 0
2005-09-06 | 3:59 | 315 | 11.7 | -46.7 | 54 | 0 | 684.5 | 0 | -46.7 | 0
2005-09-06 | 4:59 | 323 | 13.4 | -46.1 | 55 | 0 | 684.5 | 0 | -46.1 | 0
2005-09-06 | 5:59 | 294 | 13.4 | -43.9 | 57 | 0 | 684.9 | 0 | -43.9 | 0
2005-09-06 | 6:59 | 298 | 14.4 | -42.1 | 59 | 0 | 685.4 | 0 | -42.1 | 0
2005-09-06 | 7:59 | 310 | 11.8 | -42.8 | 58 | 0 | 685.6 | 0 | -42.8 | 0
2005-09-06 | 8:59 | 304 | 16.3 | -41.6 | 59 | 0 | 685.7 | 0 | -41.6 | 0
2005-09-06 | 9:59 | 295 | 18.5 | -40.9 | 60 | 0 | 685.9 | 0 | -40.9 | 0
2005-09-06 | 10:59 | 299 | 20 | -41 | 60 | 0 | 686 | 0 | -41 | 0
2005-09-06 | 11:59 | 312 | 18.8 | -41.5 | 60 | 0 | 686.3 | 0 | -41.5 | 0
2005-09-06 | 12:59 | 299 | 20.4 | -41.3 | 60 | 0 | 686.3 | 0 | -41.3 | 0
2005-09-06 | 13:59 | 301 | 21.8 | -41.1 | 60 | 0 | 686.3 | 0 | -41.1 | 0
2005-09-06 | 14:59 | 315 | 19.7 | -41.1 | 60 | 0 | 686.3 | 0 | -41.1 | 0
2005-09-06 | 15:59 | 302 | 23.7 | -40.4 | 61 | 0 | 685.7 | 0 | -40.4 | 0
2005-09-06 | 16:59 | 296 | 20.2 | -40 | 61 | 0 | 686 | 0 | -40 | 0
2005-09-06 | 17:59 | 296 | 15.7 | -39.6 | 62 | 0 | 686.2 | 0 | -39.6 | 0
2005-09-06 | 18:59 | 289 | 13.6 | -39.7 | 61 | 0 | 686.2 | 0 | -39.7 | 0
2005-09-06 | 19:59 | 299 | 19.6 | -39.3 | 62 | 0 | 686 | 0 | -39.3 | 0
2005-09-06 | 20:59 | 300 | 16.8 | -39.5 | 62 | 0 | 686 | 0 | -39.5 | 0
2005-09-06 | 21:59 | 309 | 17 | -39.3 | 62 | 0 | 686 | 0 | -39.3 | 0
2005-09-06 | 22:59 | 304 | 14.5 | -39.1 | 62 | 0 | 685.7 | 0 | -39.1 | 0
2005-09-06 | 23:59 | 280 | 18.6 | -37.8 | 63 | 0 | 685.9 | 0 | -37.8 | 0
2005-09-07 | 0:59 | 282 | 19.6 | -37.7 | 64 | 0 | 685.9 | 0 | -37.7 | 0
2005-09-07 | 1:59 | 262 | 15.9 | -37.9 | 63 | 0 | 686.8 | 0 | -37.9 | 0
2005-09-07 | 2:59 | 271 | 23.6 | -37.7 | 64 | 0 | 686.5 | 0 | -37.7 | 0
2005-09-07 | 3:59 | 249 | 14.9 | -37.3 | 64 | 0 | 687.5 | 0 | -37.3 | 0
2005-09-07 | 4:59 | 231 | 9.8 | -37.9 | 64 | 0 | 688.7 | 0 | -37.9 | 0
2005-09-07 | 5:59 | 258 | 10.9 | -40.2 | 62 | 0 | 689.3 | 0 | -40.2 | 0
2005-09-07 | 6:59 | 256 | 6 | -43.3 | 59 | 0 | 690.1 | 0 | -43.3 | 0
2005-09-07 | 7:59 | 259 | 14.6 | -44.4 | 58 | 0 | 690.5 | 0 | -44.4 | 0
2005-09-07 | 8:59 | 245 | 9.7 | -43.2 | 59 | 0 | 691.1 | 0 | -43.2 | 0
2005-09-07 | 9:59 | 241 | 10.6 | -44.8 | 57 | 0 | 691.9 | 0 | -44.8 | 0
2005-09-07 | 10:59 | 228 | 7.5 | -45 | 57 | 0 | 692.3 | 0 | -45 | 0
2005-09-07 | 11:59 | 223 | 9.4 | -44.3 | 57 | 0 | 692.3 | 0 | -44.3 | 0
2005-09-07 | 12:59 | 220 | 7.3 | -43.8 | 58 | 0 | 692.7 | 0 | -43.8 | 0
2005-09-07 | 13:59 | 138 | 4.4 | -45.8 | 56 | 0 | 692.7 | 0 | -45.8 | 0
2005-09-07 | 14:59 | 239 | 1.4 | -46.4 | 56 | 0 | 693.1 | 0 | -46.4 | 0
2005-09-07 | 15:59 | 323 | 4.2 | -44.5 | 57 | 0 | 693.7 | 0 | -44.5 | 0
2005-09-07 | 16:59 | 243 | 4.4 | -41.5 | 60 | 0 | 693.3 | 0 | -41.5 | 0
2005-09-07 | 17:59 | 279 | 2.5 | -40.8 | 61 | 0 | 693.4 | 0 | -40.8 | 0
2005-09-07 | 18:59 | 309 | 8.8 | -40.7 | 61 | 0 | 693.2 | 0 | -40.7 | 0
2005-09-07 | 19:59 | 316 | 6.7 | -40.4 | 61 | 0 | 693.2 | 0 | -40.4 | 0
2005-09-07 | 20:59 | 289 | 5.3 | -38.3 | 63 | 0 | 693.1 | 0 | -38.3 | 0
2005-09-07 | 21:59 | 278 | 8.3 | -37 | 64 | 0 | 692.7 | 0 | -37 | 0
2005-09-07 | 22:59 | 288 | 7.8 | -37.1 | 64 | 0 | 692.5 | 0 | -37.1 | 0
2005-09-07 | 23:59 | 280 | 10.6 | -36.2 | 65 | 0 | 692 | 0 | -36.2 | 0
2005-09-08 | 0:59 | 274 | 11 | -36 | 65 | 0 | 691.8 | 0 | -36 | 0
2005-09-08 | 1:59 | 269 | 10.8 | -36.4 | 65 | 0 | 691.5 | 0 | -36.4 | 0
2005-09-08 | 2:59 | 264 | 9.9 | -38 | 64 | 0 | 691.1 | 0 | -38 | 0
2005-09-08 | 3:59 | 249 | 8.4 | -39 | 63 | 0 | 691.2 | 0 | -39 | 0
2005-09-08 | 4:59 | 266 | 10 | -39.5 | 62 | 0 | 690.8 | 0 | -39.5 | 0
2005-09-08 | 5:59 | 245 | 12.8 | -38.3 | 63 | 0 | 690.7 | 0 | -38.3 | 0
2005-09-08 | 6:59 | 253 | 7.9 | -37.9 | 64 | 0 | 690.2 | 0 | -37.9 | 0
2005-09-08 | 7:59 | 265 | 7.8 | -37.4 | 64 | 0 | 689.8 | 0 | -37.4 | 0
2005-09-08 | 8:59 | 246 | 7.6 | -36 | 65 | 0 | 689.4 | 0 | -36 | 0
2005-09-08 | 9:59 | 253 | 9.4 | -35.9 | 66 | 0 | 689 | 0 | -35.9 | 0
2005-09-08 | 10:59 | 253 | 7.7 | -35.7 | 66 | 0 | 688.5 | 0 | -35.7 | 0
2005-09-08 | 11:59 | 240 | 6.4 | -35.2 | 66 | 0 | 688 | 0 | -35.2 | 0
2005-09-08 | 12:59 | 252 | 6.8 | -36.1 | 65 | 0 | 687.3 | 0 | -36.1 | 0
2005-09-08 | 13:59 | 245 | 5.3 | -38.2 | 64 | 0 | 686.9 | 0 | -38.2 | 0
2005-09-08 | 14:59 | 218 | 8.9 | -39 | 63 | 0 | 686.6 | 0 | -39 | 0
2005-09-08 | 15:59 | 124 | 6.9 | -41.1 | 61 | 0 | 686.5 | 0 | -41.1 | 0
2005-09-08 | 16:59 | 181 | 8 | -42.6 | 60 | 0 | 685.9 | 0 | -42.6 | 0
2005-09-08 | 17:59 | 186 | 9.9 | -38.8 | 63 | 0 | 685.5 | 0 | -38.8 | 0
2005-09-08 | 18:59 | 183 | 8.9 | -38.6 | 63 | 0 | 685 | 0 | -38.6 | 0
2005-09-08 | 19:59 | 179 | 5.4 | -39.7 | 62 | 0 | 684.4 | 0 | -39.7 | 0
2005-09-08 | 20:59 | 168 | 8.5 | -41.2 | 61 | 0 | 683.7 | 0 | -41.2 | 0
2005-09-08 | 21:59 | 185 | 8.4 | -46.5 | 56 | 0 | 683.2 | 0 | -46.5 | 0
2005-09-08 | 22:59 | 184 | 7.4 | -47.3 | 55 | 0 | 682.4 | 0 | -47.3 | 0
2005-09-08 | 23:59 | 150 | 10.7 | -48.6 | 54 | 0 | 681.6 | 0 | -48.6 | 0
2005-09-09 | 0:59 | 132 | 8.7 | -49.7 | 53 | 0 | 680.9 | 0 | -49.7 | 0
2005-09-09 | 1:59 | 158 | 12.9 | -51.4 | 51 | 0 | 680.3 | 0 | -51.4 | 0
2005-09-09 | 2:59 | 143 | 11 | -50.9 | 51 | 0 | 679.7 | 0 | -50.9 | 0
2005-09-09 | 3:59 | 132 | 11.2 | -48.7 | 53 | 0 | 678.9 | 0 | -48.7 | 0
2005-09-09 | 4:59 | 123 | 6.1 | -53.1 | 49 | 0 | 678.2 | 0 | -53.1 | 0
2005-09-09 | 5:59 | 154 | 9.1 | -54.4 | 48 | 0 | 677.4 | 0 | -54.4 | 0
2005-09-09 | 6:59 | 138 | 6.5 | -53.7 | 48 | 0 | 676.7 | 0 | -53.7 | 0
2005-09-09 | 7:59 | 134 | 7.8 | -54.5 | 48 | 0 | 676.1 | 0 | -54.5 | 0
2005-09-09 | 8:59 | 138 | 12.8 | -54.4 | 47 | 0 | 675.1 | 0 | -54.4 | 0
2005-09-09 | 9:59 | 141 | 11.8 | -54.7 | 47 | 0 | 674.3 | 0 | -54.7 | 0
2005-09-09 | 10:59 | 119 | 15.9 | -54.3 | 47 | 0 | 673.5 | 0 | -54.3 | 0
2005-09-09 | 11:59 | 121 | 11.2 | -55.7 | 46 | 0 | 672.9 | 0 | -55.7 | 0
2005-09-09 | 12:59 | 172 | 6.4 | -55.6 | 46 | 0 | 672.7 | 0 | -55.6 | 0
2005-09-09 | 13:59 | 145 | 10.6 | -58.8 | 43 | 0 | 672 | 0 | -58.8 | 0
2005-09-09 | 14:59 | 138 | 9.2 | -59.3 | 42 | 0 | 671.3 | 0 | -59.3 | 0
2005-09-09 | 15:59 | 140 | 10.5 | -59.3 | 42 | 0 | 670.4 | 0 | -59.3 | 0
2005-09-09 | 16:59 | 123 | 11 | -60 | 41 | 0 | 670 | 0 | -60 | 0
2005-09-09 | 17:59 | 125 | 9.5 | -60.1 | 41 | 0 | 669.7 | 0 | -60.1 | 0
2005-09-09 | 18:59 | 154 | 10.5 | -61.4 | 39 | 0 | 669.2 | 0 | -61.4 | 0
2005-09-09 | 19:59 | 156 | 9.2 | -60.8 | 40 | 0 | 668.8 | 0 | -60.8 | 0
2005-09-09 | 20:59 | 122 | 10.3 | -61.2 | 40 | 0 | 668.3 | 0 | -61.2 | 0
2005-09-09 | 21:59 | 129 | 7.7 | -61.2 | 39 | 0 | 667.9 | 0 | -61.2 | 0
2005-09-09 | 22:59 | 115 | 10.5 | -61.8 | 39 | 0 | 667.5 | 0 | -61.8 | 0
2005-09-09 | 23:59 | 124 | 7.5 | -60.1 | 40 | 0 | 667.4 | 0 | -60.1 | 0
2005-09-10 | 0:59 | 176 | 2.4 | -60.9 | 40 | 0 | 667.1 | 0 | -60.9 | 0
2005-09-10 | 1:59 | 99 | 5.7 | -61.7 | 39 | 0 | 667.1 | 0 | -61.7 | 0
2005-09-10 | 2:59 | 91 | 4.9 | -61.8 | 39 | 0 | 667.3 | 0 | -61.8 | 0
2005-09-10 | 3:59 | 66 | 5.5 | -61.9 | 38 | 0 | 667.3 | 0 | -61.9 | 0
2005-09-10 | 4:59 | 50 | 3 | -60.5 | 40 | 0 | 667.6 | 0 | -60.5 | 0
2005-09-10 | 5:59 | 4 | 6.4 | -60.2 | 40 | 0 | 667.7 | 0 | -60.2 | 0
2005-09-10 | 6:59 | 348 | 7.8 | -59.9 | 40 | 0 | 668.1 | 0 | -59.9 | 0
2005-09-10 | 7:59 | 1 | 8.4 | -61 | 39 | 0 | 668.7 | 0 | -61 | 0
2005-09-10 | 8:59 | 35 | 5.8 | -62.4 | 38 | 0 | 669.5 | 0 | -62.4 | 0
2005-09-10 | 9:59 | 47 | 6.5 | -63.3 | 37 | 0 | 670 | 0 | -63.3 | 0
2005-09-10 | 10:59 | 72 | 4.2 | -62.7 | 37 | 0 | 670.7 | 0 | -62.7 | 0
2005-09-10 | 11:59 | 56 | 3.3 | -62.8 | 37 | 0 | 671.3 | 0 | -62.8 | 0
2005-09-10 | 12:59 | 65 | 3.2 | -63.3 | 36 | 0 | 672.2 | 0 | -63.3 | 0
2005-09-10 | 13:59 | 55 | 7.3 | -63 | 37 | 0 | 672.6 | 0 | -63 | 0
2005-09-10 | 14:59 | 63 | 7.4 | -62.5 | 37 | 0 | 673.2 | 0 | -62.5 | 0
2005-09-10 | 15:59 | 65 | 5.6 | -62.4 | 37 | 0 | 673.8 | 0 | -62.4 | 0
2005-09-10 | 16:59 | 60 | 5.8 | -62.2 | 37 | 0 | 674.3 | 0 | -62.2 | 0
2005-09-10 | 17:59 | 41 | 2.9 | -63.1 | 36 | 0 | 674.9 | 0 | -63.1 | 0
2005-09-10 | 18:59 | 109 | 3.7 | -64.6 | 35 | 0 | 675.7 | 0 | -64.6 | 0
2005-09-10 | 19:59 | 89 | 5.6 | -64.9 | 35 | 0 | 676.3 | 0 | -64.9 | 0
2005-09-10 | 20:59 | 60 | 6.1 | -63.3 | 36 | 0 | 676.3 | 0 | -63.3 | 0
2005-09-10 | 21:59 | 74 | 7.5 | -64.4 | 35 | 0 | 676.7 | 0 | -64.4 | 0
2005-09-10 | 22:59 | 61 | 4.1 | -63.6 | 36 | 0 | 677.7 | 0 | -63.6 | 0
2005-09-10 | 23:59 | 48 | 5.9 | -61.9 | 38 | 0 | 678.1 | 0 | -61.9 | 0
2005-09-11 | 0:59 | 62 | 4.6 | -60.4 | 39 | 0 | 678.8 | 0 | -60.4 | 0
2005-09-11 | 1:59 | 51 | 3.8 | -59.6 | 40 | 0 | 679.1 | 0 | -59.6 | 0
2005-09-11 | 2:59 | 47 | 5.2 | -59.4 | 40 | 0 | 679.5 | 0 | -59.4 | 0
2005-09-11 | 3:59 | 67 | 4.7 | -59.5 | 40 | 0 | 679.9 | 0 | -59.5 | 0
2005-09-11 | 4:59 | 64 | 5.3 | -60.2 | 39 | 0 | 680.5 | 0 | -60.2 | 0
2005-09-11 | 5:59 | 64 | 7.9 | -60.4 | 39 | 0 | 680.9 | 0 | -60.4 | 0
2005-09-11 | 6:59 | 63 | 6.5 | -61.4 | 38 | 0 | 681.6 | 0 | -61.4 | 0
2005-09-11 | 7:59 | 49 | 5.9 | -62.4 | 37 | 0 | 682 | 0 | -62.4 | 0
2005-09-11 | 8:59 | 53 | 6.5 | -62.5 | 37 | 0 | 682.4 | 0 | -62.5 | 0
2005-09-11 | 9:59 | 59 | 6.8 | -61.9 | 38 | 0 | 682.9 | 0 | -61.9 | 0
2005-09-11 | 10:59 | 34 | 7.2 | -59.4 | 40 | 0 | 683.3 | 0 | -59.4 | 0
2005-09-11 | 11:59 | 23 | 7.4 | -59.7 | 40 | 0 | 683.6 | 0 | -59.7 | 0
2005-09-11 | 12:59 | 38 | 7.2 | -59.3 | 40 | 0 | 684.1 | 0 | -59.3 | 0
2005-09-11 | 13:59 | 32 | 10 | -59.6 | 40 | 0 | 684 | 0 | -59.6 | 0
2005-09-11 | 14:59 | 48 | 6.1 | -61.9 | 38 | 0 | 684.4 | 0 | -61.9 | 0
2005-09-11 | 15:59 | 30 | 9.3 | -59.9 | 40 | 0 | 684.6 | 0 | -59.9 | 0
2005-09-11 | 16:59 | 32 | 10.1 | -58.9 | 41 | 0 | 684.7 | 0 | -58.9 | 0
2005-09-11 | 17:59 | 11 | 10.8 | -58.4 | 41 | 0 | 685.1 | 0 | -58.4 | 0
2005-09-11 | 18:59 | 20 | 11.5 | -59 | 41 | 0 | 684.9 | 0 | -59 | 0
2005-09-11 | 19:59 | 12 | 12.8 | -58 | 42 | 0 | 684.6 | 0 | -58 | 0
2005-09-11 | 20:59 | 5 | 18 | -57.5 | 42 | 0 | 684.3 | 0 | -57.5 | 0
2005-09-11 | 21:59 | 4 | 17.4 | -56.4 | 43 | 0 | 684.4 | 0 | -56.4 | 0
2005-09-11 | 22:59 | 7 | 20.3 | -54.9 | 45 | 0 | 683.5 | 0 | -54.9 | 0
2005-09-11 | 23:59 | 1 | 22.3 | -52.9 | 47 | 0 | 682.9 | 0 | -52.9 | 0
2005-09-12 | 0:59 | 2 | 22.7 | -52.6 | 48 | 0 | 682.7 | 0 | -52.6 | 0
2005-09-12 | 1:59 | 345 | 20.5 | -50.5 | 50 | 0 | 682.7 | 0 | -50.5 | 0
2005-09-12 | 2:59 | 346 | 24.3 | -49.8 | 51 | 0 | 682.4 | 0 | -49.8 | 0
2005-09-12 | 3:59 | 339 | 26.8 | -48.7 | 52 | 0 | 681.6 | 0 | -48.7 | 0
2005-09-12 | 4:59 | 340 | 25.3 | -47 | 54 | 0 | 682.2 | 0 | -47 | 0
2005-09-12 | 5:59 | 344 | 17 | -46.2 | 55 | 0 | 682.9 | 0 | -46.2 | 0
2005-09-12 | 6:59 | 335 | 25.2 | -44.9 | 56 | 0 | 682.2 | 0 | -44.9 | 0
2005-09-12 | 7:59 | 336 | 22.6 | -44.8 | 57 | 0 | 682.8 | 0 | -44.8 | 0
2005-09-12 | 8:59 | 339 | 23.6 | -44.2 | 57 | 0 | 683.1 | 0 | -44.2 | 0
2005-09-12 | 9:59 | 337 | 18.6 | -44.2 | 57 | 0 | 683.4 | 0 | -44.2 | 0
2005-09-12 | 10:59 | 337 | 23.1 | -44 | 58 | 0 | 683.1 | 0 | -44 | 0
2005-09-12 | 11:59 | 329 | 23.9 | -43.7 | 58 | 0 | 683.2 | 0 | -43.7 | 0
2005-09-12 | 12:59 | 324 | 20.8 | -43.4 | 58 | 0 | 683.7 | 0 | -43.4 | 0
2005-09-12 | 13:59 | 327 | 18.5 | -42.5 | 59 | 0 | 684 | 0 | -42.5 | 0
2005-09-12 | 14:59 | 316 | 20.9 | -41.3 | 60 | 0 | 684.8 | 0 | -41.3 | 0
2005-09-12 | 15:59 | 322 | 10.5 | -41 | 61 | 0 | 685.9 | 0 | -41 | 0
2005-09-12 | 16:59 | 337 | 13.5 | -40.6 | 61 | 0 | 686.2 | 0 | -40.6 | 0
2005-09-12 | 17:59 | 340 | 16.5 | -41 | 61 | 0 | 686.4 | 0 | -41 | 0
2005-09-12 | 18:59 | 357 | 13 | -41.7 | 60 | 0 | 687.4 | 0 | -41.7 | 0
2005-09-12 | 19:59 | 343 | 11.9 | -41.6 | 60 | 0 | 688 | 0 | -41.6 | 0
2005-09-12 | 20:59 | 339 | 13.8 | -41.2 | 61 | 0 | 688.1 | 0 | -41.2 | 0
2005-09-12 | 21:59 | 333 | 14.7 | -40.7 | 61 | 0 | 688.8 | 0 | -40.7 | 0
2005-09-12 | 22:59 | 340 | 14.4 | -40.3 | 61 | 0 | 689.3 | 0 | -40.3 | 0
2005-09-12 | 23:59 | 340 | 17.5 | -40.3 | 61 | 0 | 689.4 | 0 | -40.3 | 0
2005-09-13 | 0:59 | 350 | 17.3 | -41.8 | 60 | 0 | 690 | 0 | -41.8 | 0
2005-09-13 | 1:59 | 350 | 19.5 | -42.6 | 59 | 0 | 690.2 | 0 | -42.6 | 0
2005-09-13 | 2:59 | 353 | 15.7 | -42.4 | 60 | 0 | 690.8 | 0 | -42.4 | 0
2005-09-13 | 3:59 | 350 | 19 | -42.4 | 60 | 0 | 691.2 | 0 | -42.4 | 0
2005-09-13 | 4:59 | 7 | 16.9 | -43.4 | 59 | 0 | 691.7 | 0 | -43.4 | 0
2005-09-13 | 5:59 | 7 | 17.9 | -44.7 | 57 | 0 | 692 | 0 | -44.7 | 0
2005-09-13 | 6:59 | 9 | 16.3 | -44.7 | 57 | 0 | 692.3 | 0 | -44.7 | 0
2005-09-13 | 7:59 | 14 | 16.4 | -45.1 | 57 | 0 | 692.4 | 0 | -45.1 | 0
2005-09-13 | 8:59 | 12 | 16.3 | -45.9 | 56 | 0 | 692.8 | 0 | -45.9 | 0
2005-09-13 | 9:59 | 12 | 20.2 | -46.6 | 55 | 0 | 693.1 | 0 | -46.6 | 0
2005-09-13 | 10:59 | 14 | 20.6 | -47.1 | 55 | 0 | 693.5 | 0 | -47.1 | 0
2005-09-13 | 11:59 | 14 | 18.8 | -47.1 | 55 | 0 | 693.8 | 0 | -47.1 | 0
2005-09-13 | 12:59 | 20 | 17.2 | -46.3 | 56 | 0 | 694 | 0 | -46.3 | 0
2005-09-13 | 13:59 | 20 | 19.5 | -45.2 | 56 | 0 | 694.3 | 0 | -45.2 | 0
2005-09-13 | 14:59 | 15 | 16.6 | -45.7 | 56 | 0 | 694.5 | 0 | -45.7 | 0
2005-09-13 | 15:59 | 19 | 18.5 | -46.1 | 56 | 0 | 694.7 | 0 | -46.1 | 0
2005-09-13 | 16:59 | 19 | 16.2 | -46.4 | 56 | 0 | 694.8 | 0 | -46.4 | 0
2005-09-13 | 17:59 | 21 | 19.3 | -46.7 | 55 | 0 | 694.9 | 0 | -46.7 | 0
2005-09-13 | 18:59 | 13 | 17.3 | -47.2 | 55 | 0 | 695.2 | 0 | -47.2 | 0
2005-09-13 | 19:59 | 27 | 13.9 | -47.9 | 54 | 0 | 695.3 | 0 | -47.9 | 0
2005-09-13 | 20:59 | 27 | 15.8 | -48.6 | 53 | 0 | 695.6 | 0 | -48.6 | 0
2005-09-13 | 21:59 | 46 | 13.5 | -49 | 53 | 0 | 696 | 0 | -49 | 0
2005-09-13 | 22:59 | 36 | 13 | -49.2 | 53 | 0 | 696 | 0 | -49.2 | 0
2005-09-13 | 23:59 | 40 | 16 | -49.8 | 52 | 1 | 696.2 | 0 | -49.8 | 0
2005-09-14 | 0:59 | 37 | 17.6 | -50 | 52 | 1 | 695.9 | 1 | -49.9688 | 0.18764
2005-09-14 | 1:59 | 39 | 16.6 | -49.9 | 52 | 0 | 695.8 | 0 | -49.9 | 0
2005-09-14 | 2:59 | 45 | 13 | -50.8 | 51 | 1 | 696 | 1 | -50.7687 | 0.18665
2005-09-14 | 3:59 | 42 | 18.5 | -50.9 | 51 | 1 | 696 | 1 | -50.8687 | 0.18653
2005-09-14 | 4:59 | 42 | 17.9 | -50.4 | 51 | 1 | 695.7 | 1 | -50.3687 | 0.18715
2005-09-14 | 5:59 | 40 | 14.6 | -51.2 | 50 | 1 | 695.8 | 1 | -51.1688 | 0.18616
2005-09-14 | 6:59 | 48 | 13.5 | -52.2 | 49 | 1 | 695.9 | 1 | -52.1688 | 0.18493
2005-09-14 | 7:59 | 51 | 14.1 | -52.3 | 49 | 2 | 696 | 1 | -52.2687 | 0.1848
2005-09-14 | 8:59 | 42 | 13.4 | -52.5 | 49 | 2 | 695.8 | 2 | -52.4375 | 0.36919
2005-09-14 | 9:59 | 54 | 13.5 | -53.6 | 48 | 2 | 695.2 | 2 | -53.5375 | 0.36648
2005-09-14 | 10:59 | 65 | 14.4 | -53.6 | 48 | 2 | 695 | 2 | -53.5375 | 0.36648
2005-09-14 | 11:59 | 71 | 15.7 | -54.6 | 47 | 2 | 694.3 | 2 | -54.5375 | 0.36402
2005-09-14 | 12:59 | 78 | 15 | -55.1 | 46 | 2 | 693.6 | 2 | -55.0375 | 0.36279
2005-09-14 | 13:59 | 82 | 15.3 | -55.2 | 46 | 1 | 692.7 | 2 | -55.1375 | 0.36254
2005-09-14 | 14:59 | 82 | 13.1 | -54.5 | 47 | 1 | 692.1 | 1 | -54.4688 | 0.18209
2005-09-14 | 15:59 | 89 | 13.5 | -54.4 | 47 | 1 | 690.7 | 1 | -54.3687 | 0.18222
2005-09-14 | 16:59 | 92 | 13.7 | -55.9 | 45 | 1 | 689.7 | 1 | -55.8687 | 0.18037
2005-09-14 | 17:59 | 89 | 13 | -56 | 45 | 1 | 688.9 | 1 | -55.9688 | 0.18025
2005-09-14 | 18:59 | 92 | 14.6 | -55.4 | 46 | 1 | 687.8 | 1 | -55.3687 | 0.18099
2005-09-14 | 19:59 | 85 | 17.9 | -54.6 | 46 | 1 | 686.7 | 1 | -54.5688 | 0.18197
2005-09-14 | 20:59 | 72 | 14.4 | -54.3 | 47 | 1 | 686.6 | 1 | -54.2687 | 0.18234
2005-09-14 | 21:59 | 69 | 14 | -55.4 | 45 | 1 | 685.9 | 1 | -55.3687 | 0.18099
2005-09-14 | 22:59 | 71 | 15.5 | -55.6 | 45 | 1 | 685.6 | 1 | -55.5688 | 0.18074
2005-09-14 | 23:59 | 60 | 15.4 | -55.8 | 45 | 1 | 685.3 | 1 | -55.7687 | 0.18049
2005-09-15 | 0:59 | 57 | 15.4 | -55.3 | 46 | 1 | 684.8 | 1 | -55.2687 | 0.18111
2005-09-15 | 1:59 | 58 | 14.5 | -54.2 | 47 | 1 | 684.2 | 1 | -54.1688 | 0.18246
2005-09-15 | 2:59 | 55 | 15.3 | -52.9 | 48 | 1 | 683.7 | 1 | -52.8687 | 0.18407
2005-09-15 | 3:59 | 44 | 16.7 | -52 | 49 | 1 | 683.1 | 1 | -51.9688 | 0.18517
2005-09-15 | 4:59 | 53 | 15.2 | -51.5 | 49 | 0 | 682.6 | 1 | -51.4688 | 0.18579
2005-09-15 | 5:59 | 46 | 24.2 | -49.7 | 51 | 0 | 682.2 | 0 | -49.7 | 0
2005-09-15 | 6:59 | 34 | 24.8 | -49.3 | 52 | 1 | 681.6 | 0 | -49.3 | 0
2005-09-15 | 7:59 | 27 | 25.4 | -49.4 | 52 | 1 | 681.6 | 1 | -49.3687 | 0.18838
2005-09-15 | 8:59 | 30 | 24.4 | -49.6 | 52 | 1 | 681.3 | 1 | -49.5688 | 0.18813
2005-09-15 | 9:59 | 30 | 21 | -49.1 | 52 | 1 | 681.4 | 1 | -49.0688 | 0.18875
2005-09-15 | 10:59 | 25 | 21.1 | -49.7 | 52 | 1 | 681.4 | 1 | -49.6688 | 0.18801
2005-09-15 | 11:59 | 26 | 23.5 | -49.7 | 52 | 1 | 681.3 | 1 | -49.6688 | 0.18801
2005-09-15 | 12:59 | 31 | 18.5 | -49.7 | 52 | 1 | 681.4 | 1 | -49.6688 | 0.18801
2005-09-15 | 13:59 | 34 | 24.4 | -49.6 | 52 | 1 | 681.2 | 1 | -49.5688 | 0.18813
2005-09-15 | 14:59 | 28 | 22.5 | -49.9 | 52 | 1 | 681.2 | 1 | -49.8687 | 0.18776
2005-09-15 | 15:59 | 34 | 24.4 | -50.1 | 51 | 1 | 681.3 | 1 | -50.0688 | 0.18752
2005-09-15 | 16:59 | 38 | 16.8 | -50.4 | 51 | 1 | 681.9 | 1 | -50.3687 | 0.18715
2005-09-15 | 17:59 | 34 | 18.3 | -50.8 | 51 | 1 | 682.2 | 1 | -50.7687 | 0.18665
2005-09-15 | 18:59 | 32 | 19.5 | -51.1 | 50 | 2 | 682.2 | 1 | -51.0688 | 0.18628
2005-09-15 | 19:59 | 29 | 20.5 | -51.7 | 50 | 2 | 682.3 | 2 | -51.6375 | 0.37117
2005-09-15 | 20:59 | 38 | 15.4 | -52.4 | 49 | 2 | 682.6 | 2 | -52.3375 | 0.36944
2005-09-15 | 21:59 | 32 | 16.3 | -52.6 | 49 | 2 | 682.9 | 2 | -52.5375 | 0.36895
2005-09-15 | 22:59 | 37 | 18.3 | -52.8 | 49 | 2 | 683.1 | 2 | -52.7375 | 0.36845
2005-09-15 | 23:59 | 36 | 16.4 | -52.8 | 49 | 2 | 683.1 | 2 | -52.7375 | 0.36845
2005-09-16 | 0:59 | 33 | 19 | -53 | 48 | 2 | 683.2 | 2 | -52.9375 | 0.36796
2005-09-16 | 1:59 | 35 | 17 | -53.3 | 48 | 2 | 683 | 2 | -53.2375 | 0.36722
2005-09-16 | 2:59 | 37 | 21.2 | -53.2 | 48 | 2 | 683.1 | 2 | -53.1375 | 0.36747
2005-09-16 | 3:59 | 37 | 16.9 | -53.4 | 48 | 2 | 683.6 | 2 | -53.3375 | 0.36698
2005-09-16 | 4:59 | 34 | 13.2 | -53.7 | 47 | 1 | 683.9 | 2 | -53.6375 | 0.36624
2005-09-16 | 5:59 | 34 | 15.4 | -54.1 | 47 | 1 | 683.8 | 1 | -54.0688 | 0.18259
2005-09-16 | 6:59 | 37 | 12 | -54.5 | 47 | 1 | 684.2 | 1 | -54.4688 | 0.18209
2005-09-16 | 7:59 | 38 | 12.6 | -54.5 | 47 | 1 | 684.5 | 1 | -54.4688 | 0.18209
2005-09-16 | 8:59 | 33 | 13.7 | -54.4 | 47 | 1 | 684.6 | 1 | -54.3687 | 0.18222
2005-09-16 | 9:59 | 37 | 14.3 | -53.8 | 47 | 1 | 684.7 | 1 | -53.7687 | 0.18296
2005-09-16 | 10:59 | 47 | 12.9 | -53.8 | 47 | 2 | 684.7 | 1 | -53.7687 | 0.18296
2005-09-16 | 11:59 | 46 | 14.5 | -53.5 | 47 | 2 | 684.8 | 2 | -53.4375 | 0.36673
2005-09-16 | 12:59 | 50 | 10.7 | -53.9 | 47 | 3 | 684.9 | 3 | -53.8062 | 0.54873
2005-09-16 | 13:59 | 48 | 10 | -55.2 | 46 | 2 | 685 | 2 | -55.1375 | 0.36254
2005-09-16 | 14:59 | 63 | 14 | -57.2 | 44 | 2 | 685.1 | 2 | -57.1375 | 0.35761
2005-09-16 | 15:59 | 63 | 11 | -56.8 | 44 | 2 | 685.2 | 2 | -56.7375 | 0.3586
2005-09-16 | 16:59 | 66 | 13.2 | -56.7 | 44 | 1 | 685.1 | 1 | -56.6688 | 0.17938
2005-09-16 | 17:59 | 72 | 11.8 | -57.9 | 43 | 1 | 685 | 1 | -57.8687 | 0.17791
2005-09-16 | 18:59 | 68 | 12.2 | -55.4 | 45 | 2 | 685 | 2 | -55.3375 | 0.36205
2005-09-16 | 19:59 | 71 | 11.1 | -56.9 | 44 | 3 | 685.2 | 2 | -56.8375 | 0.35835
2005-09-16 | 20:59 | 92 | 5.5 | -56.7 | 44 | 4 | 685.1 | 3 | -56.6063 | 0.53838
2005-09-16 | 21:59 | 79 | 10.2 | -56.5 | 44 | 3 | 685.2 | 3 | -56.4062 | 0.53912
2005-09-16 | 22:59 | 71 | 12.8 | -56 | 44 | 5 | 684.7 | 5 | -55.8438 | 0.902
2005-09-16 | 23:59 | 91 | 11.6 | -56.3 | 44 | 4 | 684.7 | 4 | -56.175 | 0.71997
2005-09-17 | 0:59 | 75 | 10.7 | -56.5 | 44 | 2 | 684.5 | 3 | -56.4062 | 0.53912
2005-09-17 | 1:59 | 82 | 9.3 | -56.6 | 44 | 1 | 684.3 | 1 | -56.5688 | 0.17951
2005-09-17 | 2:59 | 80 | 12 | -56.2 | 44 | 1 | 684 | 1 | -56.1688 | 0.18
2005-09-17 | 3:59 | 88 | 11.7 | -56.7 | 44 | 2 | 683.6 | 2 | -56.6375 | 0.35885
2005-09-17 | 4:59 | 87 | 12.9 | -55.9 | 45 | 1 | 683.5 | 2 | -55.8375 | 0.36082
2005-09-17 | 5:59 | 83 | 14.2 | -56.3 | 44 | 1 | 683.2 | 1 | -56.2687 | 0.17988
2005-09-17 | 6:59 | 88 | 14.6 | -56.9 | 43 | 1 | 682.8 | 1 | -56.8687 | 0.17914
2005-09-17 | 7:59 | 82 | 13 | -57.2 | 43 | 1 | 682.6 | 1 | -57.1688 | 0.17877
2005-09-17 | 8:59 | 80 | 13 | -56.3 | 44 | 1 | 682 | 1 | -56.2687 | 0.17988
2005-09-17 | 9:59 | 72 | 14 | -52.3 | 48 | 2 | 681.7 | 1 | -52.2687 | 0.1848
2005-09-17 | 10:59 | 76 | 14 | -53.2 | 47 | 1 | 681.5 | 1 | -53.1688 | 0.1837
2005-09-17 | 11:59 | 76 | 14.6 | -53.7 | 47 | 2 | 681.3 | 2 | -53.6375 | 0.36624
2005-09-17 | 12:59 | 72 | 10.7 | -54.8 | 46 | 3 | 681.4 | 3 | -54.7062 | 0.54541
2005-09-17 | 13:59 | 77 | 12 | -53.5 | 47 | 4 | 681 | 3 | -53.4062 | 0.55021
2005-09-17 | 14:59 | 80 | 11.1 | -53.8 | 47 | 4 | 680.8 | 4 | -53.675 | 0.73229
2005-09-17 | 15:59 | 85 | 11.4 | -54.3 | 46 | 4 | 680.5 | 4 | -54.175 | 0.72983
2005-09-17 | 16:59 | 84 | 14.2 | -51.8 | 49 | 7 | 680.1 | 8 | -51.55 | 1.4855
2005-09-17 | 17:59 | 80 | 14.4 | -51.9 | 49 | 3 | 679.4 | 5 | -51.7437 | 0.92726
2005-09-17 | 18:59 | 71 | 14.9 | -50.6 | 50 | 2 | 679.1 | 3 | -50.5063 | 0.56093
2005-09-17 | 19:59 | 71 | 19 | -49.4 | 51 | 2 | 678.5 | 2 | -49.3375 | 0.37683
2005-09-17 | 20:59 | 62 | 17.3 | -49.5 | 51 | 2 | 678.4 | 2 | -49.4375 | 0.37659
2005-09-17 | 21:59 | 73 | 16.9 | -50.4 | 51 | 2 | 677.6 | 2 | -50.3375 | 0.37437
2005-09-17 | 22:59 | 70 | 13.3 | -50.3 | 51 | 2 | 677 | 2 | -50.2375 | 0.37461
2005-09-17 | 23:59 | 84 | 13.3 | -52.2 | 49 | 2 | 676.4 | 2 | -52.1375 | 0.36993
2005-09-18 | 0:59 | 74 | 13.6 | -51.9 | 49 | 1 | 676.1 | 1 | -51.8687 | 0.1853
2005-09-18 | 1:59 | 78 | 12.5 | -52 | 49 | 1 | 675.6 | 1 | -51.9688 | 0.18517
2005-09-18 | 2:59 | 86 | 8.3 | -53.2 | 48 | 1 | 675 | 1 | -53.1688 | 0.1837
2005-09-18 | 3:59 | 90 | 9.6 | -52.9 | 48 | 1 | 674.1 | 1 | -52.8687 | 0.18407
2005-09-18 | 4:59 | 76 | 12.4 | -52.2 | 49 | 1 | 673.8 | 1 | -52.1688 | 0.18493
2005-09-18 | 5:59 | 80 | 13.6 | -53.6 | 48 | 1 | 673.3 | 1 | -53.5688 | 0.1832
2005-09-18 | 6:59 | 79 | 12.7 | -54.4 | 47 | 2 | 673 | 2 | -54.3375 | 0.36451
2005-09-18 | 7:59 | 71 | 9.5 | -53.9 | 47 | 2 | 672.8 | 2 | -53.8375 | 0.36574
2005-09-18 | 8:59 | 67 | 14.3 | -53.5 | 47 | 2 | 671.8 | 2 | -53.4375 | 0.36673
2005-09-18 | 9:59 | 63 | 15.4 | -54.3 | 47 | 1 | 671.1 | 1 | -54.2687 | 0.18234
2005-09-18 | 10:59 | 68 | 14 | -52.4 | 48 | 2 | 670.5 | 2 | -52.3375 | 0.36944
2005-09-18 | 11:59 | 63 | 12.6 | -50 | 51 | 4 | 670.3 | 3 | -49.9062 | 0.56315
2005-09-18 | 12:59 | 70 | 11.8 | -51 | 50 | 4 | 670.2 | 4 | -50.875 | 0.74609
2005-09-18 | 13:59 | 66 | 11.2 | -51.2 | 50 | 6 | 669.8 | 5 | -51.0438 | 0.93157
2005-09-18 | 14:59 | 62 | 10.9 | -51.3 | 50 | 4 | 669.5 | 5 | -51.1437 | 0.93095
2005-09-18 | 15:59 | 66 | 11.3 | -52.8 | 48 | 2 | 669.3 | 3 | -52.7062 | 0.5528
2005-09-18 | 16:59 | 68 | 13.7 | -53.6 | 48 | 2 | 669 | 2 | -53.5375 | 0.36648
2005-09-18 | 17:59 | 51 | 13.3 | -52 | 49 | 2 | 668.7 | 2 | -51.9375 | 0.37043
2005-09-18 | 18:59 | 56 | 13.5 | -50.8 | 50 | 2 | 668.4 | 2 | -50.7375 | 0.37338
2005-09-18 | 19:59 | 55 | 15.3 | -50.2 | 51 | 2 | 668.5 | 2 | -50.1375 | 0.37486
2005-09-18 | 20:59 | 50 | 12.8 | -51 | 50 | 2 | 668.9 | 2 | -50.9375 | 0.37289
2005-09-18 | 21:59 | 42 | 11.9 | -50.8 | 50 | 2 | 669.1 | 2 | -50.7375 | 0.37338
2005-09-18 | 22:59 | 63 | 12.5 | -54.4 | 47 | 3 | 669.2 | 2 | -54.3375 | 0.36451
2005-09-18 | 23:59 | 63 | 13.3 | -55.4 | 46 | 2 | 669.1 | 2 | -55.3375 | 0.36205
2005-09-19 | 0:59 | 64 | 14.2 | -55.9 | 45 | 3 | 669 | 3 | -55.8062 | 0.54134
2005-09-19 | 1:59 | 59 | 11.2 | -55.1 | 46 | 3 | 669.2 | 3 | -55.0063 | 0.5443
2005-09-19 | 2:59 | 62 | 6.3 | -55.5 | 45 | 3 | 669.6 | 3 | -55.4062 | 0.54282
2005-09-19 | 3:59 | 82 | 7.3 | -56.9 | 44 | 3 | 669.6 | 3 | -56.8062 | 0.53764
2005-09-19 | 4:59 | 71 | 12.7 | -56.7 | 44 | 3 | 669.7 | 3 | -56.6063 | 0.53838
2005-09-19 | 5:59 | 56 | 11.3 | -55.7 | 45 | 3 | 670 | 3 | -55.6063 | 0.54208
2005-09-19 | 6:59 | 64 | 15.1 | -55.2 | 45 | 3 | 669.9 | 3 | -55.1063 | 0.54393
2005-09-19 | 7:59 | 66 | 10.6 | -55.2 | 45 | 3 | 670.3 | 3 | -55.1063 | 0.54393
2005-09-19 | 8:59 | 45 | 17.2 | -50.5 | 50 | 2 | 669.9 | 3 | -50.4062 | 0.5613
2005-09-19 | 9:59 | 47 | 16.3 | -50.7 | 50 | 2 | 670.1 | 2 | -50.6375 | 0.37363
2005-09-19 | 10:59 | 36 | 15.5 | -50.9 | 50 | 2 | 670 | 2 | -50.8375 | 0.37314
2005-09-19 | 11:59 | 34 | 15.6 | -51.1 | 50 | 4 | 670.2 | 3 | -51.0063 | 0.55908
2005-09-19 | 12:59 | 32 | 18.6 | -51.5 | 49 | 6 | 669.8 | 5 | -51.3438 | 0.92972
2005-09-19 | 13:59 | 44 | 17.4 | -52.5 | 49 | 3 | 670.2 | 6 | -52.3125 | 1.1085
2005-09-19 | 14:59 | 26 | 14.4 | -52.9 | 48 | 3 | 670.3 | 3 | -52.8062 | 0.55243
2005-09-19 | 15:59 | 32 | 18.3 | -53.7 | 47 | 2 | 670.6 | 2 | -53.6375 | 0.36624
2005-09-19 | 16:59 | 28 | 19 | -54.1 | 47 | 3 | 670.6 | 2 | -54.0375 | 0.36525
2005-09-19 | 17:59 | 18 | 16.6 | -54.5 | 47 | 3 | 670.9 | 3 | -54.4062 | 0.54651
2005-09-19 | 18:59 | 29 | 16.7 | -55 | 46 | 3 | 671.1 | 3 | -54.9062 | 0.54467
2005-09-19 | 19:59 | 29 | 11.5 | -55.3 | 46 | 3 | 671.6 | 3 | -55.2062 | 0.54356
2005-09-19 | 20:59 | 22 | 17 | -55.8 | 45 | 3 | 671.8 | 3 | -55.7062 | 0.54171
2005-09-19 | 21:59 | 29 | 13.2 | -56.7 | 44 | 3 | 672 | 3 | -56.6063 | 0.53838
2005-09-19 | 22:59 | 32 | 13.4 | -57 | 44 | 4 | 672.4 | 4 | -56.875 | 0.71652
2005-09-19 | 23:59 | 34 | 9.5 | -57.2 | 43 | 4 | 673.1 | 4 | -57.075 | 0.71553
2005-09-20 | 0:59 | 34 | 13.1 | -57.4 | 43 | 5 | 673 | 4 | -57.275 | 0.71455
2005-09-20 | 1:59 | 26 | 13.4 | -57.6 | 43 | 5 | 673.2 | 5 | -57.4438 | 0.89215
2005-09-20 | 2:59 | 32 | 11.9 | -57.6 | 43 | 4 | 673.5 | 4 | -57.475 | 0.71356
2005-09-20 | 3:59 | 25 | 12 | -58.1 | 42 | 4 | 673.9 | 4 | -57.975 | 0.7111
2005-09-20 | 4:59 | 30 | 13 | -57.9 | 42 | 8 | 674.3 | 4 | -57.775 | 0.71208
2005-09-20 | 5:59 | 18 | 16.7 | -57.8 | 42 | 7 | 674.2 | 5 | -57.6437 | 0.89091
2005-09-20 | 6:59 | 14 | 16.4 | -56.6 | 44 | 16 | 674.2 | 13 | -56.1938 | 2.3396
2005-09-20 | 7:59 | 12 | 15.2 | -55.3 | 45 | 4 | 674.4 | 11 | -54.9562 | 1.9964
2005-09-20 | 8:59 | 12 | 12.5 | -54.8 | 45 | 2 | 675.1 | 3 | -54.7062 | 0.54541
2005-09-20 | 9:59 | 20 | 13.5 | -54.4 | 46 | 2 | 675 | 2 | -54.3375 | 0.36451
2005-09-20 | 10:59 | 12 | 14.6 | -53.5 | 47 | 2 | 674.8 | 2 | -53.4375 | 0.36673
2005-09-20 | 11:59 | 10 | 16.2 | -53 | 47 | 2 | 674.7 | 2 | -52.9375 | 0.36796
2005-09-20 | 12:59 | 7 | 17.4 | -52.4 | 48 | 2 | 674.4 | 2 | -52.3375 | 0.36944
2005-09-20 | 13:59 | 3 | 18.3 | -51.7 | 49 | 2 | 674 | 2 | -51.6375 | 0.37117
2005-09-20 | 14:59 | 3 | 17.6 | -50.9 | 49 | 2 | 673.9 | 2 | -50.8375 | 0.37314
2005-09-20 | 15:59 | 3 | 20.7 | -50.7 | 50 | 2 | 673.9 | 2 | -50.6375 | 0.37363
2005-09-20 | 16:59 | 1 | 18.4 | -49.7 | 51 | 2 | 673.5 | 2 | -49.6375 | 0.37609
2005-09-20 | 17:59 | 1 | 16.9 | -49.1 | 52 | 3 | 673.1 | 2 | -49.0375 | 0.37757
2005-09-20 | 18:59 | 359 | 13.8 | -48.1 | 53 | 3 | 672.7 | 3 | -48.0063 | 0.57017
2005-09-20 | 19:59 | 344 | 18.4 | -46.9 | 54 | 4 | 672.3 | 4 | -46.775 | 0.76629
2005-09-20 | 20:59 | 352 | 18.3 | -47.2 | 54 | 4 | 671.7 | 4 | -47.075 | 0.76481
2005-09-20 | 21:59 | 352 | 17.4 | -46.6 | 54 | 4 | 671.4 | 4 | -46.475 | 0.76777
2005-09-20 | 22:59 | 2 | 10 | -46.1 | 55 | 4 | 671 | 4 | -45.975 | 0.77024
2005-09-20 | 23:59 | 355 | 15.7 | -45.5 | 56 | 4 | 670.4 | 4 | -45.375 | 0.77319
2005-09-21 | 0:59 | 348 | 15.2 | -45.3 | 56 | 4 | 669.7 | 4 | -45.175 | 0.77418
2005-09-21 | 1:59 | 353 | 16.5 | -45.1 | 56 | 4 | 669.2 | 4 | -44.975 | 0.77516
2005-09-21 | 2:59 | 0 | 17.3 | -45 | 56 | 4 | 669.1 | 4 | -44.875 | 0.77566
2005-09-21 | 3:59 | 14 | 14.7 | -44.7 | 57 | 4 | 668.4 | 4 | -44.575 | 0.77713
2005-09-21 | 4:59 | 6 | 14.7 | -45.2 | 56 | 4 | 668.1 | 4 | -45.075 | 0.77467
2005-09-21 | 5:59 | 7 | 15.3 | -45.4 | 56 | 4 | 667.6 | 4 | -45.275 | 0.77368
2005-09-21 | 6:59 | 9 | 14.6 | -45.5 | 56 | 4 | 667 | 4 | -45.375 | 0.77319
2005-09-21 | 7:59 | 9 | 12.4 | -46.3 | 55 | 4 | 666.7 | 4 | -46.175 | 0.76925
2005-09-21 | 8:59 | 27 | 11.5 | -46.8 | 55 | 4 | 666.1 | 4 | -46.675 | 0.76679
2005-09-21 | 9:59 | 11 | 10.3 | -47.2 | 54 | 4 | 665.8 | 4 | -47.075 | 0.76481
2005-09-21 | 10:59 | 20 | 9.2 | -47.6 | 54 | 4 | 665.6 | 4 | -47.475 | 0.76284
2005-09-21 | 11:59 | 23 | 13.4 | -47.7 | 54 | 3 | 665.1 | 3 | -47.6063 | 0.57165
2005-09-21 | 12:59 | 23 | 12.4 | -48.4 | 53 | 4 | 664.8 | 4 | -48.275 | 0.7589
2005-09-21 | 13:59 | 18 | 13.2 | -49.2 | 52 | 4 | 664.5 | 4 | -49.075 | 0.75496
2005-09-21 | 14:59 | 22 | 15.1 | -49.4 | 52 | 5 | 664 | 6 | -49.2125 | 1.1314
2005-09-21 | 15:59 | 29 | 13 | -49.5 | 52 | 6 | 663.6 | 6 | -49.3125 | 1.1307
2005-09-21 | 16:59 | 15 | 15.3 | -48.9 | 53 | 7 | 663.2 | 8 | -48.65 | 1.5141
2005-09-21 | 17:59 | 24 | 14.2 | -50 | 52 | 6 | 663 | 7 | -49.7812 | 1.3151
2005-09-21 | 18:59 | 23 | 15.6 | -49.3 | 52 | 6 | 662.8 | 6 | -49.1125 | 1.1322
2005-09-21 | 19:59 | 20 | 18 | -48.6 | 53 | 6 | 662.6 | 6 | -48.4125 | 1.1373
2005-09-21 | 20:59 | 32 | 14.4 | -49.1 | 52 | 5 | 662.8 | 6 | -48.9125 | 1.1336
2005-09-21 | 21:59 | 32 | 16.9 | -49.4 | 52 | 8 | 662.5 | 6 | -49.2125 | 1.1314
2005-09-21 | 22:59 | 26 | 16.1 | -48 | 53 | 19 | 662.4 | 12 | -47.625 | 2.2863
2005-09-21 | 23:59 | 21 | 16.3 | -48.1 | 53 | 11 | 662.4 | 15 | -47.6313 | 2.8578
2005-09-22 | 0:59 | 21 | 18.7 | -47.7 | 54 | 5 | 662.3 | 6 | -47.5125 | 1.144
2005-09-22 | 1:59 | 28 | 20 | -47.8 | 54 | 5 | 662 | 5 | -47.6437 | 0.95251
2005-09-22 | 2:59 | 26 | 16.7 | -47.6 | 54 | 5 | 662.1 | 6 | -47.4125 | 1.1447
2005-09-22 | 3:59 | 24 | 17.8 | -47.5 | 54 | 5 | 662 | 4 | -47.375 | 0.76334
2005-09-22 | 4:59 | 24 | 19.4 | -47.6 | 54 | 5 | 662 | 5 | -47.4438 | 0.95375
2005-09-22 | 5:59 | 25 | 18.3 | -47.8 | 54 | 4 | 662 | 4 | -47.675 | 0.76186
2005-09-22 | 6:59 | 26 | 19.3 | -48.2 | 53 | 4 | 662.1 | 4 | -48.075 | 0.75989
2005-09-22 | 7:59 | 36 | 20 | -48.4 | 53 | 5 | 662 | 4 | -48.275 | 0.7589
2005-09-22 | 8:59 | 30 | 23.1 | -48.6 | 53 | 6 | 662.1 | 5 | -48.4438 | 0.94759
2005-09-22 | 9:59 | 30 | 22.7 | -49 | 52 | 6 | 662.2 | 5 | -48.8438 | 0.94512
2005-09-22 | 10:59 | 32 | 17.3 | -50.1 | 51 | 5 | 662.4 | 5 | -49.9438 | 0.93835
2005-09-22 | 11:59 | 38 | 20 | -49.8 | 52 | 6 | 662.4 | 6 | -49.6125 | 1.1285
2005-09-22 | 12:59 | 39 | 18.7 | -49.8 | 52 | 6 | 662.3 | 6 | -49.6125 | 1.1285
2005-09-22 | 13:59 | 27 | 20.1 | -50.2 | 51 | 6 | 662 | 5 | -50.0438 | 0.93773
2005-09-22 | 14:59 | 40 | 23.9 | -50.5 | 51 | 6 | 662.1 | 6 | -50.3125 | 1.1233
2005-09-22 | 15:59 | 50 | 17.9 | -51.5 | 50 | 7 | 662.4 | 7 | -51.2812 | 1.3022
2005-09-22 | 16:59 | 40 | 19 | -51.8 | 49 | 7 | 662.2 | 7 | -51.5812 | 1.2996
2005-09-22 | 17:59 | 54 | 21.1 | -52.5 | 49 | 9 | 661.9 | 8 | -52.25 | 1.4786
2005-09-22 | 18:59 | 44 | 18.7 | -53 | 48 | 8 | 662.3 | 9 | -52.7188 | 1.6583
2005-09-22 | 19:59 | 47 | 19.7 | -53.3 | 48 | 8 | 662.3 | 9 | -53.0187 | 1.6549
2005-09-22 | 20:59 | 43 | 17.7 | -53.7 | 48 | 9 | 662.5 | 8 | -53.45 | 1.4668
2005-09-22 | 21:59 | 57 | 18.6 | -54.3 | 47 | 9 | 662.5 | 9 | -54.0187 | 1.6438
2005-09-22 | 22:59 | 48 | 19.8 | -54.9 | 46 | 8 | 662.8 | 8 | -54.65 | 1.455
2005-09-22 | 23:59 | 42 | 17.1 | -55.1 | 46 | 8 | 663 | 8 | -54.85 | 1.453
2005-09-23 | 0:59 | 56 | 16.6 | -55.6 | 45 | 8 | 663.1 | 7 | -55.3813 | 1.2668
2005-09-23 | 1:59 | 51 | 15.3 | -56.1 | 45 | 8 | 663 | 8 | -55.85 | 1.4431
2005-09-23 | 2:59 | 57 | 16.6 | -56.2 | 45 | 9 | 663.1 | 9 | -55.9188 | 1.6228
2005-09-23 | 3:59 | 55 | 11.1 | -56.9 | 44 | 13 | 663.4 | 11 | -56.5562 | 1.9747
2005-09-23 | 4:59 | 51 | 11.7 | -57.6 | 43 | 10 | 663.5 | 11 | -57.2563 | 1.9653
2005-09-23 | 5:59 | 63 | 9 | -59 | 42 | 9 | 663.7 | 10 | -58.6875 | 1.769
2005-09-23 | 6:59 | 58 | 11.2 | -59 | 41 | 8 | 663.5 | 9 | -58.7188 | 1.5917
2005-09-23 | 7:59 | 59 | 14.9 | -58.8 | 42 | 10 | 663.6 | 9 | -58.5187 | 1.5939
2005-09-23 | 8:59 | 61 | 13.9 | -59.6 | 41 | 9 | 663.7 | 8 | -59.35 | 1.4086
2005-09-23 | 9:59 | 68 | 6.3 | -61.1 | 39 | 11 | 664.2 | 10 | -60.7875 | 1.7431
2005-09-23 | 10:59 | 68 | 10.3 | -62.3 | 38 | 10 | 664 | 11 | -61.9562 | 1.9016
2005-09-23 | 11:59 | 68 | 8.1 | -63 | 37 | 10 | 664.2 | 10 | -62.6875 | 1.7197
2005-09-23 | 12:59 | 68 | 9.5 | -63.9 | 36 | 10 | 664.4 | 10 | -63.5875 | 1.7086
2005-09-23 | 13:59 | 68 | 7.6 | -64 | 36 | 9 | 664.5 | 9 | -63.7188 | 1.5363
2005-09-23 | 14:59 | 68 | 9.6 | -64.2 | 36 | 10 | 664.6 | 9 | -63.9188 | 1.5341
2005-09-23 | 15:59 | 68 | 8.9 | -64.9 | 35 | 9 | 664.8 | 10 | -64.5875 | 1.6963
2005-09-23 | 16:59 | 68 | 10.7 | -66 | 34 | 11 | 664.9 | 10 | -65.6875 | 1.6827
2005-09-23 | 17:59 | 68 | 6.7 | -65.8 | 34 | 9 | 665.3 | 10 | -65.4875 | 1.6852
2005-09-23 | 18:59 | 68 | 6.4 | -66.2 | 34 | 9 | 665.7 | 9 | -65.9188 | 1.5119
2005-09-23 | 19:59 | 68 | 10 | -66.1 | 34 | 16 | 665.8 | 13 | -65.6937 | 2.1874
2005-09-23 | 20:59 | 46 | 12.5 | -61.7 | 38 | 21 | 665.9 | 18 | -61.1375 | 3.1298
2005-09-23 | 21:59 | 24 | 15.6 | -60.7 | 39 | 15 | 666.1 | 25 | -59.9188 | 4.3845
2005-09-23 | 22:59 | 25 | 12 | -60.9 | 38 | 10 | 666.2 | 11 | -60.5562 | 1.9205
2005-09-23 | 23:59 | 18 | 10.9 | -61.2 | 38 | 12 | 666.4 | 12 | -60.825 | 2.0912
2005-09-24 | 0:59 | 18 | 12.3 | -61.5 | 38 | 10 | 666.4 | 10 | -61.1875 | 1.7382
2005-09-24 | 1:59 | 22 | 12.9 | -62.3 | 37 | 10 | 666.5 | 10 | -61.9875 | 1.7283
2005-09-24 | 2:59 | 23 | 11.6 | -63.5 | 36 | 8 | 666.7 | 10 | -63.1875 | 1.7135
2005-09-24 | 3:59 | 21 | 13.2 | -63.9 | 35 | 11 | 666.5 | 11 | -63.5562 | 1.8799
2005-09-24 | 4:59 | 17 | 13.9 | -63.8 | 35 | 9 | 666.6 | 15 | -63.3312 | 2.5676
2005-09-24 | 5:59 | 14 | 16.1 | -61.7 | 37 | 31 | 666.4 | 21 | -61.0438 | 3.6539
2005-09-24 | 6:59 | 7 | 17.6 | -60.7 | 38 | 14 | 666.5 | 29 | -59.7938 | 5.0905
2005-09-24 | 7:59 | 3 | 17.4 | -59.6 | 40 | 8 | 666.4 | 9 | -59.3188 | 1.5851
2005-09-24 | 8:59 | 3 | 18.5 | -58.4 | 41 | 6 | 666.3 | 6 | -58.2125 | 1.0649
2005-09-24 | 9:59 | 350 | 12.2 | -57.2 | 42 | 8 | 666.8 | 8 | -56.95 | 1.4323
2005-09-24 | 10:59 | 350 | 10.3 | -55.5 | 44 | 8 | 667.1 | 8 | -55.25 | 1.4491
2005-09-24 | 11:59 | 323 | 14.1 | -54.7 | 45 | 8 | 667.2 | 8 | -54.45 | 1.4569
2005-09-24 | 12:59 | 339 | 14 | -53.7 | 46 | 6 | 667.6 | 7 | -53.4813 | 1.2832
2005-09-24 | 13:59 | 336 | 12.5 | -53 | 47 | 6 | 667.6 | 6 | -52.8125 | 1.1048
2005-09-24 | 14:59 | 332 | 10.7 | -52.4 | 47 | 7 | 667.8 | 7 | -52.1812 | 1.2944
2005-09-24 | 15:59 | 336 | 13.5 | -52.1 | 48 | 8 | 668.1 | 7 | -51.8813 | 1.297
2005-09-24 | 16:59 | 329 | 14.6 | -51.9 | 48 | 7 | 668.5 | 8 | -51.65 | 1.4845
2005-09-24 | 17:59 | 343 | 11 | -51.7 | 49 | 8 | 669 | 7 | -51.4813 | 1.3004
2005-09-24 | 18:59 | 337 | 12.3 | -51.4 | 49 | 8 | 669.2 | 8 | -51.15 | 1.4895
2005-09-24 | 19:59 | 327 | 12 | -51.1 | 49 | 7 | 669.5 | 8 | -50.85 | 1.4924
2005-09-24 | 20:59 | 319 | 14.3 | -50.6 | 50 | 8 | 670.1 | 8 | -50.35 | 1.4974
2005-09-24 | 21:59 | 333 | 13.5 | -50.9 | 50 | 9 | 670.4 | 9 | -50.6187 | 1.6815
2005-09-24 | 22:59 | 331 | 11.8 | -50.3 | 50 | 9 | 670.6 | 9 | -50.0187 | 1.6882
2005-09-24 | 23:59 | 324 | 13.5 | -49.3 | 51 | 9 | 670.6 | 9 | -49.0187 | 1.6993
2005-09-25 | 0:59 | 314 | 10.3 | -47.2 | 53 | 11 | 671.1 | 11 | -46.8563 | 2.1062
2005-09-25 | 1:59 | 322 | 9.7 | -46.2 | 55 | 11 | 671.3 | 10 | -45.8875 | 1.9267
2005-09-25 | 2:59 | 308 | 13.9 | -45.5 | 55 | 13 | 671.5 | 13 | -45.0938 | 2.5174
2005-09-25 | 3:59 | 307 | 13 | -45.5 | 56 | 16 | 671.7 | 15 | -45.0312 | 2.9058
2005-09-25 | 4:59 | 316 | 10.5 | -45.4 | 56 | 13 | 671.8 | 15 | -44.9312 | 2.9077
2005-09-25 | 5:59 | 303 | 13.5 | -45.4 | 56 | 12 | 671.7 | 13 | -44.9937 | 2.519
2005-09-25 | 6:59 | 301 | 15.2 | -45.8 | 56 | 9 | 672 | 11 | -45.4562 | 2.1252
2005-09-25 | 7:59 | 308 | 13.5 | -45.8 | 56 | 10 | 672.4 | 10 | -45.4875 | 1.9316
2005-09-25 | 8:59 | 311 | 14.6 | -46.3 | 55 | 13 | 672.3 | 12 | -45.925 | 2.3114
2005-09-25 | 9:59 | 314 | 11.1 | -46.4 | 55 | 11 | 672.6 | 11 | -46.0562 | 2.117
2005-09-25 | 10:59 | 312 | 11.6 | -46.8 | 55 | 8 | 672.6 | 9 | -46.5187 | 1.727
2005-09-25 | 11:59 | 315 | 8.4 | -46.6 | 55 | 7 | 672.8 | 7 | -46.3813 | 1.3444
2005-09-25 | 12:59 | 308 | 11.4 | -46.4 | 55 | 6 | 672.9 | 6 | -46.2125 | 1.1536
2005-09-25 | 13:59 | 319 | 9 | -46.6 | 55 | 6 | 672.9 | 6 | -46.4125 | 1.1521
2005-09-25 | 14:59 | 321 | 10.8 | -47.4 | 54 | 9 | 673 | 7 | -47.1812 | 1.3375
2005-09-25 | 15:59 | 306 | 12.9 | -47.6 | 54 | 11 | 672.7 | 12 | -47.225 | 2.2922
2005-09-25 | 16:59 | 304 | 12.2 | -47.4 | 54 | 11 | 672.6 | 10 | -47.0875 | 1.9119
2005-09-25 | 17:59 | 296 | 7.8 | -48.6 | 53 | 12 | 672.9 | 11 | -48.2563 | 2.0872
2005-09-25 | 18:59 | 310 | 7.9 | -49.9 | 52 | 17 | 673 | 14 | -49.4625 | 2.6357
2005-09-25 | 19:59 | 298 | 9.3 | -50.5 | 51 | 13 | 673.1 | 15 | -50.0312 | 2.8134
2005-09-25 | 20:59 | 298 | 7.5 | -51.7 | 50 | 18 | 673.2 | 18 | -51.1375 | 3.3516
2005-09-25 | 21:59 | 294 | 6.7 | -51.8 | 50 | 20 | 673.2 | 21 | -51.1437 | 3.91
2005-09-25 | 22:59 | 292 | 8 | -52.7 | 49 | 14 | 673.3 | 16 | -52.2 | 2.9582
2005-09-25 | 23:59 | 279 | 7.3 | -53.4 | 48 | 13 | 673.2 | 14 | -52.9625 | 2.5753
2005-09-26 | 0:59 | 272 | 6.3 | -53 | 48 | 14 | 673.2 | 14 | -52.5625 | 2.5822
2005-09-26 | 1:59 | 273 | 4 | -53.2 | 48 | 14 | 673.2 | 15 | -52.7313 | 2.7635
2005-09-26 | 2:59 | 333 | 3.7 | -55.5 | 46 | 26 | 673.1 | 23 | -54.7812 | 4.1793
2005-09-26 | 3:59 | 0 | 7.5 | -55.9 | 45 | 40 | 673.1 | 35 | -54.8062 | 6.3588
2005-09-26 | 4:59 | 5 | 6.8 | -54.7 | 46 | 27 | 673 | 31 | -53.7313 | 5.6731
2005-09-26 | 5:59 | 1 | 7.2 | -54.6 | 46 | 23 | 673 | 25 | -53.8188 | 4.5724
2005-09-26 | 6:59 | 7 | 8.4 | -54.4 | 46 | 33 | 672.8 | 29 | -53.4937 | 5.3156
2005-09-26 | 7:59 | 7 | 7.4 | -54.6 | 46 | 19 | 673 | 27 | -53.7563 | 4.9403
2005-09-26 | 8:59 | 8 | 6.2 | -54.3 | 46 | 14 | 673 | 15 | -53.8312 | 2.7432
2005-09-26 | 9:59 | 18 | 4.5 | -53.6 | 47 | 16 | 673 | 16 | -53.1 | 2.9405
2005-09-26 | 10:59 | 14 | 4.8 | -53.5 | 47 | 13 | 673.1 | 14 | -53.0625 | 2.5736
2005-09-26 | 11:59 | 11 | 5.3 | -53.9 | 47 | 13 | 672.8 | 14 | -53.4625 | 2.5667
2005-09-26 | 12:59 | 20 | 5.5 | -54 | 47 | 13 | 672.9 | 13 | -53.5938 | 2.3812
2005-09-26 | 13:59 | 22 | 5.6 | -54.7 | 46 | 11 | 672.7 | 12 | -54.325 | 2.1873
2005-09-26 | 14:59 | 21 | 7 | -55.3 | 45 | 12 | 672.8 | 11 | -54.9562 | 1.9964
2005-09-26 | 15:59 | 23 | 4.9 | -56 | 45 | 12 | 672.8 | 12 | -55.625 | 2.168
2005-09-26 | 16:59 | 15 | 4.1 | -54.8 | 46 | 13 | 672.8 | 12 | -54.425 | 2.1858
2005-09-26 | 17:59 | 7 | 6.9 | -54.8 | 46 | 13 | 673 | 13 | -54.3937 | 2.3684
2005-09-26 | 18:59 | 17 | 5.6 | -54.6 | 46 | 13 | 673 | 13 | -54.1938 | 2.3716
2005-09-26 | 19:59 | 6 | 1.2 | -55.3 | 45 | 14 | 673.3 | 13 | -54.8937 | 2.3604
2005-09-26 | 20:59 | 25 | 2.5 | -56 | 44 | 13 | 673.5 | 14 | -55.5625 | 2.5305
2005-09-26 | 21:59 | 25 | 3 | -56.4 | 44 | 13 | 673.4 | 13 | -55.9937 | 2.3428
2005-09-26 | 22:59 | 25 | 3.4 | -56.3 | 44 | 16 | 673.4 | 14 | -55.8625 | 2.5253
2005-09-26 | 23:59 | 25 | 3.7 | -56.2 | 44 | 16 | 673.5 | 16 | -55.7 | 2.8892
2005-09-27 | 0:59 | 25 | 3.5 | -56.3 | 44 | 18 | 673.5 | 16 | -55.8 | 2.8873
2005-09-27 | 1:59 | 23 | 5 | -56.1 | 44 | 17 | 673.6 | 18 | -55.5375 | 3.254
2005-09-27 | 2:59 | 26 | 3.6 | -58.2 | 42 | 18 | 673.5 | 17 | -57.6688 | 3.0286
2005-09-27 | 3:59 | 26 | 3.4 | -59.6 | 41 | 21 | 673.5 | 19 | -59.0063 | 3.3536
2005-09-27 | 4:59 | 45 | 4.5 | -59.1 | 41 | 23 | 673.8 | 22 | -58.4125 | 3.8992
2005-09-27 | 5:59 | 36 | 3.3 | -59.5 | 41 | 22 | 674 | 23 | -58.7812 | 4.066
2005-09-27 | 6:59 | 47 | 3.6 | -58.6 | 41 | 22 | 674.2 | 22 | -57.9125 | 3.9127
2005-09-27 | 7:59 | 46 | 1.9 | -57.6 | 42 | 19 | 674.3 | 20 | -56.975 | 3.5801
2005-09-27 | 8:59 | 46 | 3.1 | -57.1 | 43 | 18 | 674.5 | 18 | -56.5375 | 3.2318
2005-09-27 | 9:59 | 46 | 3.9 | -55.9 | 44 | 22 | 674.6 | 20 | -55.275 | 3.622
2005-09-27 | 10:59 | 46 | 0 | -55.2 | 45 | 18 | 674.7 | 20 | -54.575 | 3.6393
2005-09-27 | 11:59 | 46 | 2.7 | -55.1 | 45 | 16 | 674.8 | 16 | -54.6 | 2.9109
2005-09-27 | 12:59 | 47 | 3.2 | -54.7 | 45 | 16 | 674.9 | 16 | -54.2 | 2.9188
2005-09-27 | 13:59 | 46 | 2.7 | -53.7 | 46 | 16 | 675 | 16 | -53.2 | 2.9385
2005-09-27 | 14:59 | 47 | 3.1 | -54.1 | 46 | 19 | 675.3 | 17 | -53.5688 | 3.1145
2005-09-27 | 15:59 | 46 | 5 | -55.3 | 45 | 17 | 675.4 | 18 | -54.7375 | 3.2717
2005-09-27 | 16:59 | 46 | 6 | -55.3 | 45 | 15 | 675.4 | 16 | -54.8 | 2.907
2005-09-27 | 17:59 | 46 | 7 | -55.8 | 44 | 17 | 675.6 | 16 | -55.3 | 2.8971
2005-09-27 | 18:59 | 46 | 6.9 | -56.7 | 44 | 18 | 675.9 | 18 | -56.1375 | 3.2407
2005-09-27 | 19:59 | 46 | 7.3 | -56.8 | 43 | 18 | 676 | 19 | -56.2062 | 3.4191
2005-09-27 | 20:59 | 36 | 7.4 | -56.8 | 43 | 17 | 675.9 | 17 | -56.2687 | 3.0579
2005-09-27 | 21:59 | 38 | 7.8 | -58.8 | 41 | 15 | 676 | 16 | -58.3 | 2.838
2005-09-27 | 22:59 | 47 | 7.2 | -59.9 | 40 | 17 | 676.1 | 16 | -59.4 | 2.8163
2005-09-27 | 23:59 | 31 | 7.9 | -57.7 | 42 | 18 | 675.9 | 17 | -57.1688 | 3.0391
2005-09-28 | 0:59 | 44 | 6.2 | -60.2 | 40 | 18 | 675.9 | 18 | -59.6375 | 3.1631
2005-09-28 | 1:59 | 47 | 5.2 | -58.8 | 41 | 19 | 675.9 | 19 | -58.2062 | 3.3723
2005-09-28 | 2:59 | 47 | 6 | -59.1 | 41 | 18 | 676.1 | 19 | -58.5063 | 3.3653
2005-09-28 | 3:59 | 47 | 6 | -58.5 | 41 | 20 | 676 | 19 | -57.9062 | 3.3793
2005-09-28 | 4:59 | 55 | 5.5 | -57.9 | 42 | 20 | 676 | 20 | -57.275 | 3.5727
2005-09-28 | 5:59 | 57 | 5.8 | -58 | 42 | 20 | 675.9 | 20 | -57.375 | 3.5703
2005-09-28 | 6:59 | 57 | 6.9 | -57.7 | 42 | 22 | 675.8 | 21 | -57.0438 | 3.7574
2005-09-28 | 7:59 | 61 | 7.2 | -57.1 | 43 | 19 | 676 | 20 | -56.475 | 3.5925
2005-09-28 | 8:59 | 61 | 6.8 | -57.3 | 42 | 19 | 675.9 | 19 | -56.7062 | 3.4074
2005-09-28 | 9:59 | 62 | 8.3 | -58.7 | 41 | 24 | 675.9 | 21 | -58.0438 | 3.7315
2005-09-28 | 10:59 | 42 | 9.1 | -58.9 | 41 | 25 | 675.6 | 26 | -58.0875 | 4.6185
2005-09-28 | 11:59 | 50 | 10.3 | -59.7 | 40 | 29 | 675.6 | 27 | -58.8563 | 4.7706
2005-09-28 | 12:59 | 60 | 8.7 | -60.4 | 39 | 33 | 675.7 | 32 | -59.4 | 5.6326
2005-09-28 | 13:59 | 52 | 4.9 | -58.7 | 41 | 35 | 675.6 | 36 | -57.575 | 6.4176
2005-09-28 | 14:59 | 59 | 8.5 | -60.8 | 39 | 27 | 675.5 | 26 | -59.9875 | 4.5577
2005-09-28 | 15:59 | 63 | 8.3 | -61.4 | 38 | 19 | 675.3 | 22 | -60.7125 | 3.8368
2005-09-28 | 16:59 | 62 | 9.7 | -60.6 | 39 | 18 | 675.3 | 18 | -60.0375 | 3.1542
2005-09-28 | 17:59 | 63 | 9 | -61.5 | 38 | 16 | 675.3 | 18 | -60.9375 | 3.1343
2005-09-28 | 18:59 | 63 | 9.3 | -61.6 | 38 | 16 | 675.3 | 16 | -61.1 | 2.7828
2005-09-28 | 19:59 | 63 | 6.4 | -62.8 | 36 | 17 | 675.3 | 17 | -62.2687 | 2.9322
2005-09-28 | 20:59 | 63 | 8 | -63.8 | 35 | 21 | 675.3 | 17 | -63.2687 | 2.9113
2005-09-28 | 21:59 | 63 | 6.5 | -62.7 | 36 | 14 | 675 | 17 | -62.1688 | 2.9343
2005-09-28 | 22:59 | 63 | 8.4 | -61.7 | 37 | 20 | 674.7 | 15 | -61.2313 | 2.6064
2005-09-28 | 23:59 | 63 | 7.5 | -59.9 | 39 | 20 | 674.5 | 22 | -59.2125 | 3.8775
2005-09-29 | 0:59 | 63 | 6.6 | -59.2 | 40 | 44 | 674.6 | 27 | -58.3563 | 4.7872
2005-09-29 | 1:59 | 63 | 4.2 | -59.4 | 40 | 29 | 674.3 | 43 | -58.0562 | 7.64
2005-09-29 | 2:59 | 63 | 6.7 | -59.7 | 39 | 25 | 674.3 | 28 | -58.825 | 4.9484
2005-09-29 | 3:59 | 64 | 5.4 | -59.3 | 40 | 28 | 674.2 | 26 | -58.4875 | 4.6057
2005-09-29 | 4:59 | 64 | 5.1 | -59 | 40 | 21 | 674.1 | 22 | -58.3125 | 3.9019
2005-09-29 | 5:59 | 64 | 6.5 | -60.5 | 39 | 22 | 673.9 | 23 | -59.7812 | 4.0376
2005-09-29 | 6:59 | 64 | 4.4 | -58.9 | 40 | 43 | 673.5 | 28 | -58.025 | 4.976
2005-09-29 | 7:59 | 64 | 5.7 | -59.2 | 40 | 55 | 673.4 | 53 | -57.5438 | 9.4502
2005-09-29 | 8:59 | 64 | 3.5 | -59.9 | 39 | 54 | 673.1 | 53 | -58.2437 | 9.4045
2005-09-29 | 9:59 | 126 | 11.3 | -60.4 | 39 | 46 | 672.8 | 49 | -58.8687 | 8.657
2005-09-29 | 10:59 | 115 | 12 | -59.8 | 39 | 40 | 672.1 | 42 | -58.4875 | 7.44
2005-09-29 | 11:59 | 120 | 12.1 | -58.7 | 40 | 37 | 671.6 | 39 | -57.4813 | 6.9569
2005-09-29 | 12:59 | 133 | 14.7 | -57.9 | 41 | 35 | 670.9 | 36 | -56.775 | 6.4531
2005-09-29 | 13:59 | 124 | 14.1 | -57 | 42 | 27 | 670.6 | 31 | -56.0312 | 5.5853
2005-09-29 | 14:59 | 133 | 12.9 | -58 | 41 | 28 | 669.8 | 29 | -57.0938 | 5.187
2005-09-29 | 15:59 | 115 | 14.5 | -57.6 | 42 | 27 | 669.2 | 28 | -56.725 | 5.0208
2005-09-29 | 16:59 | 114 | 16.2 | -60.2 | 39 | 27 | 668.9 | 27 | -59.3563 | 4.754
2005-09-29 | 17:59 | 117 | 15.9 | -61.4 | 38 | 25 | 668.5 | 27 | -60.5562 | 4.7141
2005-09-29 | 18:59 | 121 | 11.7 | -62 | 37 | 26 | 668.1 | 24 | -61.25 | 4.1698
2005-09-29 | 19:59 | 124 | 17.6 | -61.9 | 37 | 25 | 667.1 | 25 | -61.1187 | 4.3475
2005-09-29 | 20:59 | 110 | 15.1 | -62.2 | 37 | 25 | 666.5 | 25 | -61.4188 | 4.3383
2005-09-29 | 21:59 | 104 | 20.5 | -63.6 | 35 | 26 | 666 | 23 | -62.8813 | 3.9498
2005-09-29 | 22:59 | 105 | 21.7 | -64 | 35 | 29 | 665.1 | 26 | -63.1875 | 4.4552
2005-09-29 | 23:59 | 108 | 23.9 | -63.7 | 35 | 21 | 664.9 | 24 | -62.95 | 4.1195
2005-09-30 | 0:59 | 107 | 20.1 | -62.9 | 36 | 24 | 664.5 | 24 | -62.15 | 4.1431
2005-09-30 | 1:59 | 106 | 18.5 | -62 | 37 | 26 | 664.3 | 27 | -61.1562 | 4.6941
2005-09-30 | 2:59 | 104 | 19.3 | -61.8 | 37 | 22 | 664.1 | 26 | -60.9875 | 4.5256
2005-09-30 | 3:59 | 101 | 17.9 | -62.2 | 37 | 26 | 664.2 | 26 | -61.3875 | 4.5128
2005-09-30 | 4:59 | 109 | 12.8 | -62.6 | 36 | 24 | 664.3 | 26 | -61.7875 | 4.5
2005-09-30 | 5:59 | 109 | 17.8 | -62.1 | 37 | 23 | 663.9 | 26 | -61.2875 | 4.516
2005-09-30 | 6:59 | 107 | 17.5 | -61.4 | 38 | 27 | 663.8 | 28 | -60.525 | 4.8897
2005-09-30 | 7:59 | 109 | 22.5 | -61.4 | 37 | 31 | 663.5 | 29 | -60.4937 | 5.0655
2005-09-30 | 8:59 | 106 | 17.3 | -61 | 38 | 29 | 663.8 | 30 | -60.0625 | 5.2561
2005-09-30 | 9:59 | 104 | 16.6 | -61.2 | 38 | 32 | 664 | 31 | -60.2313 | 5.4248
2005-09-30 | 10:59 | 108 | 15.9 | -61.5 | 37 | 30 | 663.8 | 31 | -60.5312 | 5.4134
2005-09-30 | 11:59 | 95 | 17.6 | -61.3 | 38 | 33 | 663.1 | 31 | -60.3312 | 5.421
2005-09-30 | 12:59 | 102 | 17.5 | -61.1 | 38 | 32 | 663.1 | 32 | -60.1 | 5.605
2005-09-30 | 13:59 | 98 | 16.5 | -60.9 | 38 | 31 | 662.7 | 32 | -59.9 | 5.6129
2005-09-30 | 14:59 | 100 | 13.8 | -60.8 | 38 | 32 | 662.9 | 32 | -59.8 | 5.6168
2005-09-30 | 15:59 | 106 | 14 | -61 | 38 | 30 | 662.7 | 31 | -60.0312 | 5.4325
2005-09-30 | 16:59 | 98 | 13.1 | -61.4 | 38 | 31 | 662.8 | 30 | -60.4625 | 5.2413
2005-09-30 | 17:59 | 91 | 17.1 | -61.6 | 37 | 26 | 662.6 | 28 | -60.725 | 4.8828
2005-09-30 | 18:59 | 92 | 16 | -62 | 37 | 26 | 662.7 | 27 | -61.1562 | 4.6941
2005-09-30 | 19:59 | 98 | 19.3 | -62.2 | 37 | 25 | 662.8 | 27 | -61.3563 | 4.6874
2005-09-30 | 20:59 | 94 | 15 | -62.7 | 36 | 25 | 662.9 | 25 | -61.9188 | 4.3229
2005-09-30 | 21:59 | 90 | 12.6 | -62.6 | 36 | 25 | 662.8 | 24 | -61.85 | 4.152
2005-09-30 | 22:59 | 89 | 10.9 | -62.7 | 36 | 26 | 662.7 | 25 | -61.9188 | 4.3229
2005-09-30 | 23:58 | 92 | 13.5 | -63.5 | 35 | 26 | 662.6 | 25 | -62.7188 | 4.2983
2005-10-01 | 0:59 | 86 | 15.4 | -63.3 | 35 | 28 | 662.5 | 27 | -62.4562 | 4.6509
2005-10-01 | 1:59 | 86 | 13.3 | -63.5 | 35 | 30 | 663.2 | 29 | -62.5938 | 4.9905
2005-10-01 | 2:59 | 89 | 12.9 | -64 | 35 | 31 | 663.4 | 30 | -63.0625 | 5.1452
2005-10-01 | 3:59 | 79 | 14.3 | -63.6 | 35 | 35 | 663.2 | 33 | -62.5688 | 5.6798
2005-10-01 | 4:59 | 87 | 14.6 | -64.1 | 34 | 32 | 663.4 | 36 | -62.975 | 6.1781
2005-10-01 | 5:59 | 80 | 16.6 | -63.6 | 35 | 39 | 663.5 | 31 | -62.6313 | 5.3332
2005-10-01 | 6:59 | 82 | 13 | -64 | 34 | 39 | 663.8 | 39 | -62.7812 | 6.7023
2005-10-01 | 7:59 | 83 | 14 | -64.2 | 34 | 39 | 663.8 | 39 | -62.9813 | 6.6927
2005-10-01 | 8:59 | 86 | 15.4 | -64.4 | 34 | 40 | 663.4 | 40 | -63.15 | 6.856
2005-10-01 | 9:59 | 87 | 16 | -64.2 | 34 | 40 | 663.4 | 41 | -62.9188 | 7.039
2005-10-01 | 10:59 | 82 | 14 | -64.5 | 34 | 40 | 663.4 | 41 | -63.2188 | 7.0239
2005-10-01 | 11:59 | 101 | 12.5 | -65 | 34 | 39 | 663.9 | 40 | -63.75 | 6.8264
2005-10-01 | 12:59 | 77 | 12.3 | -65 | 34 | 37 | 663.7 | 38 | -63.8125 | 6.4822
2005-10-01 | 13:59 | 93 | 11.8 | -65.4 | 34 | 35 | 663.6 | 36 | -64.275 | 6.1205
2005-10-01 | 14:59 | 86 | 10.8 | -65.6 | 35 | 32 | 663.8 | 33 | -64.5687 | 5.5985
2005-10-01 | 15:59 | 88 | 12.6 | -65.9 | 35 | 30 | 663.8 | 31 | -64.9313 | 5.2453
2005-10-01 | 16:59 | 89 | 11.5 | -66.5 | 35 | 28 | 663.6 | 29 | -65.5938 | 4.8833
2005-10-01 | 17:59 | 82 | 13.4 | -66.8 | 35 | 25 | 663.4 | 27 | -65.9562 | 4.5344
2005-10-01 | 18:59 | 84 | 12.6 | -67.1 | 35 | 23 | 663.6 | 24 | -66.35 | 4.019
2005-10-01 | 19:59 | 85 | 13.3 | -67.3 | 34 | 22 | 663.5 | 22 | -66.6125 | 3.6769
2005-10-01 | 20:59 | 101 | 8.5 | -67.7 | 34 | 22 | 663.9 | 21 | -67.0438 | 3.4986
2005-10-01 | 21:59 | 87 | 11.4 | -68 | 34 | 22 | 663.9 | 22 | -67.3125 | 3.658
2005-10-01 | 22:59 | 87 | 12.1 | -67.7 | 34 | 24 | 664.2 | 23 | -66.9813 | 3.8336
2005-10-01 | 23:59 | 80 | 11.7 | -67.7 | 34 | 28 | 664.2 | 26 | -66.8875 | 4.3367
2005-10-02 | 0:59 | 85 | 11.7 | -67.4 | 34 | 33 | 664.1 | 31 | -66.4313 | 5.1881
2005-10-02 | 1:59 | 84 | 11 | -67.7 | 34 | 40 | 664.2 | 37 | -66.5438 | 6.1871
2005-10-02 | 2:59 | 88 | 10.9 | -68.2 | 34 | 46 | 664.3 | 43 | -66.8563 | 7.1738
2005-10-02 | 3:59 | 90 | 11.9 | -68.1 | 34 | 52 | 664.3 | 48 | -66.6 | 8.0231
2005-10-02 | 4:59 | 90 | 11.1 | -68.1 | 34 | 42 | 664.6 | 53 | -66.4437 | 8.8691
2005-10-02 | 5:59 | 85 | 11.1 | -68.1 | 34 | 59 | 664.7 | 31 | -67.1312 | 5.1613
2005-10-02 | 6:59 | 97 | 10.7 | -68.3 | 34 | 58 | 664.9 | 59 | -66.4562 | 9.8722
2005-10-02 | 7:59 | 85 | 10.8 | -68 | 34 | 57 | 664.9 | 58 | -66.1875 | 9.7241
2005-10-02 | 8:59 | 90 | 11.3 | -68.7 | 33 | 57 | 664.9 | 57 | -66.9188 | 9.5051
2005-10-02 | 9:59 | 101 | 8.4 | -68.4 | 34 | 53 | 665.2 | 55 | -66.6813 | 9.1877
2005-10-02 | 10:59 | 88 | 8.2 | -68.6 | 33 | 50 | 665.2 | 52 | -66.975 | 8.6677
2005-10-02 | 11:59 | 85 | 11 | -68.7 | 33 | 47 | 665 | 48 | -67.2 | 7.9877
2005-10-02 | 12:59 | 83 | 10.1 | -68.4 | 33 | 42 | 665.1 | 45 | -66.9938 | 7.4999
2005-10-02 | 13:59 | 83 | 11.1 | -68.8 | 33 | 39 | 665 | 41 | -67.5187 | 6.8067
2005-10-02 | 14:59 | 88 | 10.9 | -68.8 | 33 | 35 | 664.9 | 37 | -67.6437 | 6.1369
2005-10-02 | 15:59 | 91 | 11.3 | -68.7 | 33 | 32 | 665.1 | 33 | -67.6688 | 5.4725
2005-10-02 | 16:59 | 91 | 9.7 | -69.3 | 33 | 29 | 665.1 | 30 | -68.3625 | 4.9493
2005-10-02 | 17:59 | 81 | 9.8 | -69.5 | 33 | 26 | 664.9 | 28 | -68.625 | 4.6103
2005-10-02 | 18:59 | 85 | 10 | -69.3 | 33 | 24 | 664.9 | 25 | -68.5187 | 4.1196
2005-10-02 | 19:59 | 82 | 9.8 | -69.5 | 33 | 22 | 664.9 | 23 | -68.7812 | 3.7826
2005-10-02 | 20:59 | 104 | 8.5 | -70 | 32 | 22 | 665.3 | 22 | -69.3125 | 3.6038
2005-10-02 | 21:59 | 94 | 9.5 | -70.1 | 32 | 23 | 665 | 22 | -69.4125 | 3.601
2005-10-02 | 22:59 | 90 | 10.3 | -70.3 | 32 | 25 | 665 | 24 | -69.55 | 3.9243
2005-10-02 | 23:59 | 78 | 11.4 | -69.8 | 32 | 31 | 664.6 | 28 | -68.925 | 4.6
2005-10-03 | 0:59 | 91 | 9.4 | -70.3 | 32 | 38 | 664.4 | 34 | -69.2375 | 5.5726
2005-10-03 | 1:59 | 78 | 8.6 | -70 | 32 | 46 | 664.5 | 42 | -68.6875 | 6.9122
2005-10-03 | 2:59 | 77 | 10 | -70.4 | 32 | 53 | 664.4 | 50 | -68.8375 | 8.2196
2005-10-03 | 3:59 | 84 | 8.7 | -70.1 | 32 | 59 | 664.7 | 56 | -68.35 | 9.2396
2005-10-03 | 4:59 | 87 | 9.3 | -70.5 | 32 | 40 | 664.6 | 60 | -68.625 | 9.8792
2005-10-03 | 5:59 | 81 | 11.6 | -70.7 | 31 | 66 | 664.4 | 32 | -69.7 | 5.2265
2005-10-03 | 6:59 | 78 | 12.2 | -70.2 | 32 | 67 | 664 | 67 | -68.1063 | 11.0746
2005-10-03 | 7:59 | 76 | 8.4 | -70.5 | 31 | 66 | 664.4 | 67 | -68.4062 | 11.0499
2005-10-03 | 8:59 | 82 | 7.1 | -70.7 | 31 | 64 | 664.7 | 65 | -68.6688 | 10.699
2005-10-03 | 9:59 | 75 | 11.9 | -71.3 | 31 | 61 | 664.4 | 62 | -69.3625 | 10.1522
2005-10-03 | 10:59 | 87 | 8.5 | -70.8 | 31 | 72 | 664.4 | 63 | -68.8312 | 10.3572
2005-10-03 | 11:59 | 81 | 9.5 | -70.8 | 31 | 30 | 664.3 | 57 | -69.0187 | 9.3576
2005-10-03 | 12:59 | 73 | 10 | -70.5 | 31 | 48 | 664.2 | 45 | -69.0938 | 7.3834
2005-10-03 | 13:59 | 85 | 8.9 | -71 | 31 | 48 | 664.1 | 49 | -69.4688 | 8.0171
2005-10-03 | 14:59 | 79 | 7.4 | -70.1 | 32 | 41 | 664.1 | 45 | -68.6937 | 7.4056
2005-10-03 | 15:59 | 82 | 8.1 | -70 | 32 | 41 | 664 | 39 | -68.7812 | 6.414
2005-10-03 | 16:59 | 82 | 7.3 | -68.6 | 33 | 46 | 664.2 | 41 | -67.3187 | 6.8168
2005-10-03 | 17:59 | 68 | 6.2 | -66.9 | 34 | 37 | 664.2 | 34 | -65.8375 | 5.715
2005-10-03 | 18:59 | 68 | 3.3 | -65.3 | 35 | 36 | 664.2 | 34 | -64.2375 | 5.782
2005-10-03 | 19:59 | 54 | 5.7 | -63.5 | 34 | 24 | 663.7 | 31 | -62.5312 | 5.337
2005-10-03 | 20:59 | 26 | 7.2 | -62.1 | 35 | 31 | 663.6 | 29 | -61.1938 | 5.0405
2005-10-03 | 21:59 | 35 | 7.1 | -61.6 | 36 | 34 | 663.2 | 32 | -60.6 | 5.5853
2005-10-03 | 22:59 | 11 | 6.8 | -60.6 | 37 | 35 | 663.3 | 34 | -59.5375 | 5.9789
2005-10-03 | 23:59 | 6 | 7.3 | -59.9 | 37 | 35 | 663.1 | 35 | -58.8062 | 6.1863
2005-10-04 | 0:59 | 15 | 7.3 | -59.1 | 39 | 34 | 662.9 | 34 | -58.0375 | 6.0417
2005-10-04 | 1:59 | 14 | 7.7 | -58.4 | 39 | 34 | 662.7 | 34 | -57.3375 | 6.071
2005-10-04 | 2:59 | 2 | 8.3 | -57.9 | 40 | 36 | 662.5 | 34 | -56.8375 | 6.092
2005-10-04 | 3:59 | 9 | 7.1 | -57.6 | 41 | 41 | 662.3 | 38 | -56.4125 | 6.8286
2005-10-04 | 4:59 | 353 | 9.1 | -57 | 41 | 38 | 662.4 | 41 | -55.7188 | 7.4027
2005-10-04 | 5:59 | 352 | 10.6 | -56.3 | 42 | 38 | 662 | 38 | -55.1125 | 6.8895
2005-10-04 | 6:59 | 349 | 7.1 | -55.7 | 43 | 40 | 661.9 | 41 | -54.4188 | 7.4684
2005-10-04 | 7:59 | 342 | 8.4 | -55.1 | 44 | 38 | 661.8 | 39 | -53.8813 | 7.1299
2005-10-04 | 8:59 | 353 | 12.2 | -55 | 44 | 39 | 661.5 | 37 | -53.8438 | 6.766
2005-10-04 | 9:59 | 345 | 12.9 | -54.6 | 44 | 39 | 661.4 | 38 | -53.4125 | 6.969
2005-10-04 | 10:59 | 1 | 10.4 | -54.3 | 45 | 41 | 661.4 | 38 | -53.1125 | 6.9831
2005-10-04 | 11:59 | 356 | 9.5 | -54.2 | 45 | 38 | 661.4 | 39 | -52.9813 | 7.1732
2005-10-04 | 12:59 | 3 | 10.4 | -54.1 | 45 | 39 | 661.4 | 38 | -52.9125 | 6.9924
2005-10-04 | 13:59 | 9 | 9.9 | -54.1 | 45 | 38 | 661.6 | 39 | -52.8813 | 7.178
2005-10-04 | 14:59 | 350 | 12.5 | -53.9 | 46 | 38 | 661.6 | 37 | -52.7437 | 6.8161
2005-10-04 | 15:59 | 340 | 11.9 | -53.6 | 46 | 33 | 661.7 | 37 | -52.4438 | 6.8298
2005-10-04 | 16:59 | 0 | 13.6 | -53.3 | 46 | 35 | 661.5 | 34 | -52.2375 | 6.2847
2005-10-04 | 17:59 | 358 | 11 | -52.8 | 47 | 38 | 661.6 | 37 | -51.6437 | 6.8663
2005-10-04 | 18:59 | 13 | 8.2 | -52.6 | 47 | 41 | 661.6 | 41 | -51.3188 | 7.625
2005-10-04 | 19:59 | 19 | 9.6 | -52.6 | 47 | 44 | 661.6 | 43 | -51.2563 | 8.0002
2005-10-04 | 20:59 | 20 | 10 | -52.3 | 48 | 38 | 661.5 | 39 | -51.0812 | 7.2644
2005-10-04 | 21:59 | 24 | 10.3 | -52.2 | 48 | 39 | 661.7 | 40 | -50.95 | 7.4572
2005-10-04 | 22:59 | 9 | 12.9 | -52.3 | 48 | 40 | 661.7 | 39 | -51.0812 | 7.2644
2005-10-04 | 23:59 | 15 | 12.5 | -53.1 | 47 | 42 | 661.5 | 42 | -51.7875 | 7.7867
2005-10-05 | 0:59 | 20 | 13.1 | -53.7 | 47 | 37 | 661.3 | 39 | -52.4813 | 7.1972
2005-10-05 | 1:59 | 26 | 16.4 | -54.2 | 46 | 38 | 661.6 | 37 | -53.0438 | 6.8025
2005-10-05 | 2:59 | 24 | 15.8 | -54.3 | 46 | 44 | 661.4 | 42 | -52.9875 | 7.7246
2005-10-05 | 3:59 | 36 | 12.4 | -54.3 | 46 | 42 | 661.3 | 42 | -52.9875 | 7.7246
2005-10-05 | 4:59 | 31 | 10.3 | -54.2 | 46 | 40 | 661.1 | 43 | -52.8563 | 7.9155
2005-10-05 | 5:59 | 36 | 12.7 | -54.5 | 46 | 47 | 661 | 41 | -53.2188 | 7.529
2005-10-05 | 6:59 | 28 | 10.3 | -54.6 | 46 | 57 | 661.2 | 54 | -52.9125 | 9.9366
2005-10-05 | 7:59 | 51 | 12.2 | -55.1 | 45 | 54 | 661.2 | 52 | -53.475 | 9.5326
2005-10-05 | 8:59 | 43 | 10.6 | -55 | 45 | 46 | 661.1 | 48 | -53.5 | 8.7978
2005-10-05 | 9:59 | 49 | 10.6 | -55.2 | 45 | 41 | 661.3 | 44 | -53.825 | 8.0471
2005-10-05 | 10:59 | 45 | 12.4 | -55.2 | 45 | 50 | 661.2 | 46 | -53.7625 | 8.4164
2005-10-05 | 11:59 | 52 | 12.4 | -55.2 | 45 | 54 | 661.4 | 53 | -53.5438 | 9.7114
2005-10-05 | 12:59 | 47 | 14.7 | -54.6 | 45 | 64 | 661.4 | 58 | -52.7875 | 10.6816
2005-10-05 | 13:59 | 54 | 11.6 | -54.4 | 46 | 48 | 661.4 | 56 | -52.65 | 10.3228
2005-10-05 | 14:59 | 55 | 14.5 | -54.4 | 46 | 67 | 661.7 | 65 | -52.3687 | 12.0043
2005-10-05 | 15:59 | 60 | 13.7 | -53.7 | 46 | 107 | 662 | 89 | -50.9188 | 16.5957
2005-10-05 | 16:59 | 62 | 13.7 | -53.2 | 47 | 71 | 662 | 103 | -49.9813 | 19.3252
2005-10-05 | 17:59 | 66 | 14.8 | -54.4 | 46 | 36 | 662.4 | 45 | -52.9937 | 8.276
2005-10-05 | 18:59 | 68 | 13 | -55 | 45 | 52 | 662.6 | 43 | -53.6562 | 7.8731
2005-10-05 | 19:59 | 62 | 8.7 | -55 | 45 | 48 | 663 | 53 | -53.3438 | 9.7245
2005-10-05 | 20:59 | 74 | 11.8 | -56 | 44 | 32 | 663.3 | 41 | -54.7188 | 7.4532
2005-10-05 | 21:59 | 68 | 14.7 | -56 | 44 | 28 | 663.5 | 31 | -55.0312 | 5.6234
2005-10-05 | 22:59 | 59 | 15.2 | -56.4 | 44 | 27 | 663.8 | 30 | -55.4625 | 5.4261
2005-10-05 | 23:59 | 68 | 12.9 | -57.4 | 43 | 29 | 664 | 27 | -56.5562 | 4.8471
2005-10-06 | 0:59 | 71 | 12.3 | -57.5 | 42 | 52 | 664.3 | 39 | -56.2812 | 7.0146
2005-10-06 | 1:59 | 64 | 12.4 | -57.7 | 42 | 61 | 664.3 | 59 | -55.8563 | 10.6427
2005-10-06 | 2:59 | 64 | 11.4 | -57.8 | 42 | 71 | 664.5 | 62 | -55.8625 | 11.1834
2005-10-06 | 3:59 | 79 | 9.9 | -59.4 | 40 | 83 | 664.6 | 77 | -56.9937 | 13.7817
2005-10-06 | 4:59 | 83 | 9.5 | -60 | 39 | 65 | 664.5 | 85 | -57.3438 | 15.177
2005-10-06 | 5:59 | 106 | 9.1 | -59.3 | 40 | 98 | 664.8 | 69 | -57.1437 | 12.3371
2005-10-06 | 6:59 | 88 | 10.3 | -60 | 39 | 101 | 664.9 | 100 | -56.875 | 17.913
2005-10-06 | 7:59 | 93 | 11.7 | -60.4 | 39 | 101 | 664.8 | 101 | -57.2437 | 18.0462
2005-10-06 | 8:59 | 96 | 9.7 | -60.6 | 39 | 100 | 664.7 | 100 | -57.475 | 17.8391
2005-10-06 | 9:59 | 93 | 9.6 | -60.7 | 38 | 95 | 664.3 | 102 | -57.5125 | 18.1911
2005-10-06 | 10:59 | 84 | 9.4 | -60.8 | 38 | 91 | 664.2 | 92 | -57.925 | 16.3609
2005-10-06 | 11:59 | 89 | 7.4 | -61.5 | 37 | 54 | 664.1 | 78 | -59.0625 | 13.7619
2005-10-06 | 12:59 | 114 | 5.9 | -62 | 37 | 71 | 663.9 | 54 | -60.3125 | 9.4443
2005-10-06 | 13:59 | 103 | 7.2 | -62.5 | 36 | 87 | 663.5 | 67 | -60.4062 | 11.7102
2005-10-06 | 14:59 | 101 | 6.5 | -61.8 | 37 | 70 | 663.5 | 84 | -59.175 | 14.8089
2005-10-06 | 15:59 | 124 | 0 | -62.3 | 36 | 64 | 662.9 | 54 | -60.6125 | 9.4244
2005-10-06 | 16:59 | 126 | 4.6 | -62.3 | 36 | 73 | 662.9 | 81 | -59.7687 | 14.2208
2005-10-06 | 17:59 | 138 | 4.2 | -61.9 | 37 | 55 | 662.5 | 67 | -59.8062 | 11.7598
2005-10-06 | 18:59 | 138 | 4.8 | -61.7 | 37 | 47 | 662.5 | 51 | -60.1063 | 8.9326
2005-10-06 | 19:59 | 125 | 6.5 | -60.7 | 38 | 48 | 662.1 | 50 | -59.1375 | 8.8171
2005-10-06 | 20:59 | 127 | 6 | -60.7 | 38 | 58 | 661.8 | 57 | -58.9188 | 10.0669
2005-10-06 | 21:59 | 104 | 4.7 | -61.9 | 37 | 34 | 661.3 | 46 | -60.4625 | 8.0367
2005-10-06 | 22:59 | 131 | 5.4 | -62.1 | 36 | 49 | 661 | 40 | -60.85 | 6.9693
2005-10-06 | 23:59 | 109 | 5.9 | -62.7 | 36 | 58 | 660.8 | 52 | -61.075 | 9.0457
2005-10-07 | 0:59 | 97 | 8.8 | -62.2 | 36 | 67 | 660.7 | 62 | -60.2625 | 10.8473
2005-10-07 | 1:59 | 103 | 7.3 | -63 | 35 | 76 | 660.3 | 71 | -60.7812 | 12.3765
2005-10-07 | 2:59 | 100 | 11.2 | -62.1 | 36 | 85 | 659.7 | 81 | -59.5688 | 14.2407
2005-10-07 | 3:59 | 90 | 5.4 | -62.4 | 36 | 93 | 659.6 | 89 | -59.6187 | 15.6417
2005-10-07 | 4:59 | 102 | 7.1 | -62.5 | 36 | 62 | 659.5 | 92 | -59.625 | 16.1683
2005-10-07 | 5:59 | 87 | 6.4 | -63.4 | 35 | 103 | 659 | 75 | -61.0562 | 13.0484
2005-10-07 | 6:59 | 94 | 10.6 | -62.9 | 35 | 103 | 658.7 | 103 | -59.6812 | 18.0943
2005-10-07 | 7:59 | 76 | 10.6 | -62.9 | 35 | 105 | 658.2 | 105 | -59.6187 | 18.4537
2005-10-07 | 8:59 | 78 | 11.7 | -62.8 | 35 | 105 | 657.8 | 105 | -59.5187 | 18.4667
2005-10-07 | 9:59 | 70 | 11.7 | -62.5 | 36 | 102 | 657.4 | 104 | -59.25 | 18.3252
2005-10-07 | 10:59 | 67 | 11.4 | -63 | 35 | 97 | 656.9 | 100 | -59.875 | 17.5434
2005-10-07 | 11:59 | 75 | 11.4 | -62.6 | 35 | 91 | 656.7 | 94 | -59.6625 | 16.5154
2005-10-07 | 12:59 | 68 | 10.6 | -63.3 | 35 | 85 | 656.5 | 88 | -60.55 | 15.365
2005-10-07 | 13:59 | 72 | 9 | -63.6 | 34 | 81 | 656.3 | 82 | -61.0375 | 14.2681
2005-10-07 | 14:59 | 65 | 10.3 | -63.9 | 34 | 78 | 655.9 | 77 | -61.4937 | 13.3549
2005-10-07 | 15:59 | 69 | 10.9 | -63.9 | 34 | 70 | 655.7 | 73 | -61.6187 | 12.6499
2005-10-07 | 16:59 | 57 | 11.2 | -62.8 | 35 | 67 | 655.4 | 68 | -60.675 | 11.8625
2005-10-07 | 17:59 | 58 | 10.4 | -62.3 | 36 | 65 | 655.3 | 66 | -60.2375 | 11.5492
2005-10-07 | 18:59 | 60 | 10.7 | -62.6 | 35 | 73 | 655 | 66 | -60.5375 | 11.5248
2005-10-07 | 19:59 | 57 | 10.3 | -61.2 | 37 | 68 | 654.9 | 85 | -58.5438 | 15.0513
2005-10-07 | 20:59 | 41 | 12.4 | -60 | 38 | 30 | 654.9 | 52 | -58.375 | 9.2187
2005-10-07 | 21:59 | 35 | 13.8 | -58.8 | 39 | 46 | 654.9 | 55 | -57.0812 | 9.8382
2005-10-07 | 22:59 | 38 | 11.2 | -58.4 | 40 | 63 | 654.8 | 56 | -56.65 | 10.0468
2005-10-07 | 23:59 | 28 | 12 | -58.5 | 40 | 61 | 655.2 | 59 | -56.6562 | 10.5846
2005-10-08 | 0:59 | 32 | 13.3 | -58.4 | 40 | 55 | 655.1 | 72 | -56.15 | 12.9617
2005-10-08 | 1:59 | 31 | 13.6 | -58.7 | 40 | 58 | 655.5 | 73 | -56.4188 | 13.1175
2005-10-08 | 2:59 | 24 | 11.1 | -58.8 | 40 | 56 | 655.8 | 69 | -56.6437 | 12.3796
2005-10-08 | 3:59 | 27 | 13.2 | -59.2 | 39 | 56 | 656.1 | 66 | -57.1375 | 11.8012
2005-10-08 | 4:59 | 29 | 11.9 | -59.1 | 40 | 80 | 656.8 | 70 | -56.9125 | 12.5359
2005-10-08 | 5:59 | 29 | 12.1 | -58.9 | 40 | 58 | 657.1 | 75 | -56.5562 | 13.4642
2005-10-08 | 6:59 | 26 | 10.6 | -58.7 | 40 | 93 | 657.4 | 75 | -56.3563 | 13.4827
2005-10-08 | 7:59 | 29 | 11.1 | -59.4 | 39 | 50 | 657.9 | 70 | -57.2125 | 12.51
2005-10-08 | 8:59 | 24 | 12 | -59.3 | 39 | 114 | 658.4 | 85 | -56.6437 | 15.2503
2005-10-08 | 9:59 | 30 | 12.8 | -59.1 | 40 | 83 | 658.9 | 70 | -56.9125 | 12.5359
2005-10-08 | 10:59 | 22 | 14.3 | -59 | 40 | 70 | 659.5 | 61 | -57.0938 | 10.9105
2005-10-08 | 11:59 | 23 | 14.9 | -58.6 | 40 | 80 | 660 | 95 | -55.6313 | 17.1629
2005-10-08 | 12:59 | 34 | 13.6 | -58.7 | 40 | 48 | 660.6 | 59 | -56.8563 | 10.57
2005-10-08 | 13:59 | 12 | 18.8 | -58.4 | 40 | 53 | 660.5 | 59 | -56.5562 | 10.5918
2005-10-08 | 14:59 | 19 | 13.6 | -58.2 | 41 | 68 | 661.2 | 60 | -56.325 | 10.7885
2005-10-08 | 15:59 | 19 | 16.7 | -58 | 41 | 74 | 661.5 | 62 | -56.0625 | 11.1681
2005-10-08 | 16:59 | 26 | 16.3 | -57.8 | 41 | 54 | 661.8 | 67 | -55.7062 | 12.0982
2005-10-08 | 17:59 | 24 | 13.5 | -57.4 | 42 | 62 | 662.6 | 53 | -55.7437 | 9.5678
2005-10-08 | 18:59 | 19 | 16.4 | -57.1 | 42 | 62 | 662.9 | 64 | -55.1 | 11.6043
2005-10-08 | 19:59 | 18 | 13 | -56.6 | 42 | 60 | 663.3 | 58 | -54.7875 | 10.5387
2005-10-08 | 20:59 | 12 | 15.4 | -55.8 | 43 | 67 | 663.7 | 66 | -53.7375 | 12.0777
2005-10-08 | 21:59 | 11 | 16.8 | -54.9 | 44 | 70 | 664 | 70 | -52.7125 | 12.8981
2005-10-08 | 22:59 | 8 | 16.6 | -54.6 | 45 | 83 | 664.4 | 76 | -52.225 | 14.0493
2005-10-08 | 23:59 | 15 | 16.7 | -54.3 | 45 | 82 | 664.8 | 80 | -51.8 | 14.8306
2005-10-09 | 0:59 | 12 | 18.1 | -54.4 | 45 | 47 | 665.1 | 66 | -52.3375 | 12.1915
2005-10-09 | 1:59 | 11 | 17.7 | -54.6 | 45 | 63 | 665.5 | 64 | -52.6 | 11.8014
2005-10-09 | 2:59 | 12 | 18.4 | -53.8 | 46 | 61 | 665.8 | 72 | -51.55 | 13.3697
2005-10-09 | 3:59 | 7 | 17 | -53.3 | 46 | 49 | 665.9 | 62 | -51.3625 | 11.5271
2005-10-09 | 4:59 | 10 | 18.3 | -52.6 | 47 | 58 | 666.2 | 62 | -50.6625 | 11.5806
2005-10-09 | 5:59 | 14 | 20.9 | -52.5 | 47 | 69 | 666.3 | 64 | -50.5 | 11.967
2005-10-09 | 6:59 | 9 | 18.4 | -52.8 | 47 | 91 | 666.5 | 79 | -50.3312 | 14.7882
2005-10-09 | 7:59 | 4 | 23.7 | -52.9 | 47 | 72 | 667 | 85 | -50.2437 | 15.9205
2005-10-09 | 8:59 | 11 | 19.4 | -52.7 | 47 | 74 | 667.2 | 78 | -50.2625 | 14.6076
2005-10-09 | 9:59 | 10 | 22.7 | -52.2 | 48 | 79 | 667.4 | 77 | -49.7938 | 14.4648
2005-10-09 | 10:59 | 17 | 21.8 | -51.8 | 48 | 73 | 667.9 | 72 | -49.55 | 13.5471
2005-10-09 | 11:59 | 10 | 21.2 | -51 | 49 | 77 | 668.1 | 72 | -48.75 | 13.6181
2005-10-09 | 12:59 | 15 | 21.2 | -50.7 | 49 | 54 | 668.2 | 77 | -48.2938 | 14.6071
2005-10-09 | 13:59 | 14 | 20.8 | -49.6 | 50 | 80 | 668.2 | 74 | -47.2875 | 14.1297
2005-10-09 | 14:59 | 16 | 19.9 | -49.9 | 50 | 72 | 668.4 | 62 | -47.9625 | 11.7868
2005-10-09 | 15:59 | 9 | 24.9 | -49.2 | 51 | 66 | 668.6 | 71 | -46.9813 | 13.5837
2005-10-09 | 16:59 | 16 | 24 | -48.8 | 52 | 56 | 669 | 61 | -46.8937 | 11.677
2005-10-09 | 17:59 | 16 | 20.8 | -47.8 | 53 | 71 | 669.5 | 68 | -45.675 | 13.1191
2005-10-09 | 18:59 | 12 | 23.3 | -47.4 | 53 | 74 | 669.5 | 68 | -45.275 | 13.1526
2005-10-09 | 19:59 | 6 | 21.2 | -45.3 | 55 | 64 | 670 | 61 | -43.3937 | 11.9401
2005-10-09 | 20:59 | 8 | 26.5 | -45.7 | 55 | 48 | 670.4 | 59 | -43.8563 | 11.515
2005-10-09 | 21:59 | 12 | 22.3 | -45 | 56 | 71 | 670.7 | 55 | -43.2812 | 10.7733
2005-10-09 | 22:59 | 14 | 22.9 | -44.6 | 56 | 57 | 670.9 | 70 | -42.4125 | 13.7863
2005-10-09 | 23:59 | 12 | 24 | -44.3 | 56 | 51 | 671.2 | 56 | -42.55 | 11.0196
2005-10-10 | 0:59 | 12 | 25 | -43.8 | 57 | 72 | 671 | 71 | -41.5812 | 14.056
2005-10-10 | 1:59 | 14 | 28.6 | -43.1 | 58 | 54 | 671.5 | 72 | -40.85 | 14.3188
2005-10-10 | 2:59 | 9 | 26.5 | -43.3 | 58 | 59 | 671.8 | 59 | -41.4562 | 11.6894
2005-10-10 | 3:59 | 7 | 23.1 | -42.3 | 59 | 78 | 671.9 | 62 | -40.3625 | 12.3674
2005-10-10 | 4:59 | 8 | 23.8 | -40.9 | 60 | 65 | 672 | 75 | -38.5562 | 15.1274
2005-10-10 | 5:59 | 15 | 22.7 | -41.1 | 60 | 62 | 672.7 | 68 | -38.975 | 13.6804
2005-10-10 | 6:59 | 9 | 24.2 | -39.5 | 61 | 60 | 673.3 | 64 | -37.5 | 12.992
2005-10-10 | 7:59 | 7 | 21.1 | -38.2 | 63 | 67 | 673.8 | 61 | -36.2938 | 12.4737
2005-10-10 | 8:59 | 7 | 21.4 | -36.2 | 64 | 62 | 674.5 | 60 | -34.325 | 12.4147
2005-10-10 | 9:59 | 8 | 20.7 | -35.5 | 65 | 59 | 675.5 | 60 | -33.625 | 12.4664
2005-10-10 | 10:59 | 14 | 21.9 | -35.2 | 66 | 55 | 675.9 | 58 | -33.3875 | 12.0679
2005-10-10 | 11:59 | 8 | 22.6 | -34.1 | 67 | 55 | 676.4 | 56 | -32.35 | 11.7233
2005-10-10 | 12:59 | 7 | 24.6 | -33.1 | 67 | 58 | 676.9 | 59 | -31.2563 | 12.4308
2005-10-10 | 13:59 | 5 | 27.1 | -32 | 69 | 55 | 677.2 | 56 | -30.25 | 11.8682
2005-10-10 | 14:59 | 1 | 21.3 | -31.4 | 69 | 53 | 677.8 | 53 | -29.7437 | 11.2655
2005-10-10 | 15:59 | 348 | 20.5 | -30.5 | 70 | 56 | 678.8 | 56 | -28.75 | 11.9717
2005-10-10 | 16:59 | 345 | 19.3 | -29.7 | 71 | 57 | 679.9 | 57 | -27.9187 | 12.2438
2005-10-10 | 17:59 | 338 | 23.7 | -28.9 | 71 | 60 | 680.9 | 58 | -27.0875 | 12.518
2005-10-10 | 18:59 | 350 | 19 | -29 | 71 | 63 | 681.7 | 61 | -27.0938 | 13.1651
2005-10-10 | 19:59 | 350 | 20.9 | -28.9 | 71 | 60 | 682.3 | 63 | -26.9312 | 13.6093
2005-10-10 | 20:59 | 358 | 26.5 | -29 | 71 | 64 | 682.9 | 61 | -27.0938 | 13.1651
2005-10-10 | 21:59 | 0 | 17.6 | -29.3 | 71 | 62 | 683.6 | 63 | -27.3313 | 13.5783
2005-10-10 | 22:59 | 6 | 22.2 | -29.2 | 71 | 59 | 683.9 | 61 | -27.2937 | 13.15
2005-10-10 | 23:59 | 1 | 19.8 | -29.2 | 71 | 61 | 684.2 | 61 | -27.2937 | 13.15
2005-10-11 | 0:59 | 3 | 25.9 | -29.3 | 71 | 61 | 684.3 | 61 | -27.3938 | 13.1425
2005-10-11 | 1:59 | 11 | 25.4 | -30.1 | 71 | 64 | 684.4 | 63 | -28.1313 | 13.5162
2005-10-11 | 2:59 | 6 | 29.7 | -30.7 | 70 | 62 | 684.5 | 63 | -28.7312 | 13.4696
2005-10-11 | 3:59 | 358 | 22.1 | -30.6 | 70 | 61 | 684.7 | 63 | -28.6313 | 13.4774
2005-10-11 | 4:59 | 349 | 20 | -30.8 | 70 | 56 | 685.5 | 60 | -28.925 | 12.8139
2005-10-11 | 5:59 | 355 | 21.6 | -31.2 | 70 | 55 | 685.9 | 55 | -29.4812 | 11.7084
2005-10-11 | 6:59 | 6 | 17.5 | -31.5 | 70 | 58 | 686.4 | 55 | -29.7812 | 11.688
2005-10-11 | 7:59 | 4 | 22.1 | -31.9 | 69 | 62 | 686 | 62 | -29.9625 | 13.1617
2005-10-11 | 8:59 | 10 | 20.9 | -32.3 | 69 | 62 | 686.1 | 64 | -30.3 | 13.5597
2005-10-11 | 9:59 | 9 | 22.2 | -32.7 | 69 | 69 | 686.2 | 66 | -30.6375 | 13.956
2005-10-11 | 10:59 | 2 | 21.3 | -32.9 | 69 | 68 | 686.4 | 69 | -30.7437 | 14.5813
2005-10-11 | 11:59 | 5 | 25.2 | -33.9 | 68 | 70 | 686.3 | 69 | -31.7437 | 14.4963
2005-10-11 | 12:59 | 1 | 21 | -34.9 | 67 | 75 | 686.6 | 70 | -32.7125 | 14.6229
2005-10-11 | 13:59 | 0 | 13.5 | -35.8 | 66 | 68 | 687 | 71 | -33.5812 | 14.7558
2005-10-11 | 14:59 | 10 | 13.3 | -36.5 | 66 | 83 | 687.2 | 85 | -33.8438 | 17.6379
2005-10-11 | 15:59 | 4 | 16 | -36.1 | 66 | 63 | 686.9 | 63 | -34.1313 | 13.0505
2005-10-11 | 16:59 | 6 | 16 | -35.9 | 66 | 89 | 686.9 | 88 | -33.15 | 18.3356
2005-10-11 | 17:59 | 4 | 15.4 | -36.5 | 66 | 72 | 687.2 | 81 | -33.9688 | 16.7954
2005-10-11 | 18:59 | 353 | 17 | -36.9 | 65 | 76 | 687.6 | 85 | -34.2437 | 17.596
2005-10-11 | 19:59 | 353 | 13.5 | -37.6 | 65 | 84 | 687.8 | 83 | -35.0063 | 17.104
2005-10-11 | 20:59 | 338 | 14.2 | -38 | 64 | 71 | 688 | 73 | -35.7188 | 14.9792
2005-10-11 | 21:59 | 342 | 18 | -38 | 64 | 85 | 688.3 | 83 | -35.4062 | 17.0631
2005-10-11 | 22:59 | 346 | 14.5 | -39.4 | 63 | 75 | 688.8 | 81 | -36.8687 | 16.506
2005-10-11 | 23:59 | 338 | 15.3 | -39.9 | 63 | 88 | 689 | 73 | -37.6187 | 14.8083
2005-10-12 | 0:59 | 341 | 15 | -40.9 | 62 | 85 | 689.3 | 81 | -38.3687 | 16.3563
2005-10-12 | 1:59 | 342 | 13.6 | -40.5 | 62 | 72 | 689.5 | 71 | -38.2812 | 14.3447
2005-10-12 | 2:59 | 350 | 12.7 | -41.7 | 61 | 108 | 689.6 | 97 | -38.6688 | 19.5513
2005-10-12 | 3:59 | 352 | 12.7 | -41.8 | 61 | 98 | 689.6 | 104 | -38.55 | 20.9775
2005-10-12 | 4:59 | 341 | 13 | -40.3 | 62 | 80 | 689.9 | 82 | -37.7375 | 16.622
2005-10-12 | 5:59 | 355 | 10.9 | -40.5 | 62 | 57 | 690.3 | 74 | -38.1875 | 14.9593
2005-10-12 | 6:59 | 7 | 12 | -41.1 | 61 | 73 | 690.7 | 76 | -38.725 | 15.3133
2005-10-12 | 7:59 | 5 | 14 | -41.8 | 61 | 135 | 690.7 | 90 | -38.9875 | 18.1051
2005-10-12 | 8:59 | 0 | 13.1 | -43.1 | 59 | 117 | 691 | 120 | -39.35 | 24.0865
2005-10-12 | 9:59 | 0 | 13.9 | -43.8 | 59 | 86 | 690.6 | 104 | -40.55 | 20.7212
2005-10-12 | 10:59 | 7 | 14.1 | -43.4 | 59 | 109 | 690.4 | 89 | -40.6187 | 17.725
2005-10-12 | 11:59 | 7 | 13.5 | -44 | 58 | 131 | 690.5 | 124 | -40.125 | 24.771
2005-10-12 | 12:59 | 10 | 13.8 | -44.9 | 58 | 120 | 690.5 | 114 | -41.3375 | 22.603
2005-10-12 | 13:59 | 10 | 13.6 | -45.4 | 57 | 103 | 690.5 | 118 | -41.7125 | 23.3416
2005-10-12 | 14:59 | 10 | 12.2 | -44.6 | 58 | 74 | 690.5 | 77 | -42.1938 | 15.1857
2005-10-12 | 15:59 | 5 | 13.2 | -43.1 | 59 | 88 | 690.5 | 84 | -40.475 | 16.7441
2005-10-12 | 16:59 | 14 | 12.5 | -44.5 | 58 | 75 | 690 | 104 | -41.25 | 20.6315
2005-10-12 | 17:59 | 13 | 13.1 | -45.9 | 57 | 81 | 689.6 | 87 | -43.1812 | 17.0521
2005-10-12 | 18:59 | 17 | 11.9 | -46.8 | 56 | 99 | 689.5 | 97 | -43.7687 | 18.9419
2005-10-12 | 19:59 | 14 | 13.7 | -47.1 | 55 | 79 | 689.3 | 90 | -44.2875 | 17.5174
2005-10-12 | 20:59 | 15 | 13.8 | -47.8 | 55 | 71 | 689 | 86 | -45.1125 | 16.6514
2005-10-12 | 21:59 | 21 | 15.2 | -47.8 | 55 | 86 | 688.8 | 82 | -45.2375 | 15.8643
2005-10-12 | 22:59 | 15 | 14.5 | -48 | 54 | 83 | 688.3 | 83 | -45.4062 | 16.0405
2005-10-12 | 23:59 | 16 | 14 | -48.5 | 54 | 64 | 688 | 70 | -46.3125 | 13.45
2005-10-13 | 0:59 | 12 | 14.1 | -48.3 | 54 | 79 | 687.6 | 70 | -46.1125 | 13.4673
2005-10-13 | 1:59 | 17 | 17.3 | -47.7 | 54 | 84 | 687.1 | 83 | -45.1063 | 16.0712
2005-10-13 | 2:59 | 14 | 18.1 | -47.8 | 54 | 76 | 686.7 | 75 | -45.4562 | 14.4898
2005-10-13 | 3:59 | 11 | 16.4 | -47.9 | 54 | 75 | 686.6 | 78 | -45.4625 | 15.0688
2005-10-13 | 4:59 | 14 | 15.3 | -47.5 | 55 | 77 | 686.7 | 72 | -45.25 | 13.9285
2005-10-13 | 5:59 | 9 | 19.3 | -46.9 | 55 | 82 | 686.4 | 81 | -44.3687 | 15.7576
2005-10-13 | 6:59 | 14 | 19.6 | -46.2 | 56 | 95 | 686.2 | 86 | -43.5125 | 16.821
2005-10-13 | 7:59 | 10 | 17.8 | -45.5 | 57 | 79 | 686.2 | 85 | -42.8438 | 16.6954
2005-10-13 | 8:59 | 8 | 17.7 | -45.9 | 56 | 86 | 686.2 | 80 | -43.4 | 15.6585
2005-10-13 | 9:59 | 10 | 20 | -45.5 | 57 | 85 | 685.8 | 84 | -42.875 | 16.4958
2005-10-13 | 10:59 | 1 | 20.7 | -44.7 | 57 | 84 | 685.7 | 87 | -41.9813 | 17.1807
2005-10-13 | 11:59 | 0 | 19 | -44 | 58 | 74 | 685.6 | 77 | -41.5938 | 15.2427
2005-10-13 | 12:59 | 6 | 19.6 | -43.3 | 59 | 77 | 685.5 | 77 | -40.8937 | 15.3091
2005-10-13 | 13:59 | 8 | 17.1 | -43 | 59 | 79 | 685.3 | 76 | -40.625 | 15.1354
2005-10-13 | 14:59 | 0 | 17.2 | -42.8 | 59 | 86 | 685.2 | 80 | -40.3 | 15.964
2005-10-13 | 15:59 | 6 | 20.6 | -42.5 | 60 | 76 | 685 | 79 | -40.0312 | 15.7906
2005-10-13 | 16:59 | 358 | 20.2 | -42.4 | 60 | 74 | 684.9 | 76 | -40.025 | 15.1916
2005-10-13 | 17:59 | 3 | 19 | -42.6 | 60 | 74 | 684.9 | 77 | -40.1938 | 15.3755
2005-10-13 | 18:59 | 9 | 16.3 | -42.8 | 59 | 73 | 684.9 | 79 | -40.3312 | 15.7614
2005-10-13 | 19:59 | 4 | 21.6 | -41.9 | 60 | 76 | 684.2 | 75 | -39.5562 | 15.035
2005-10-13 | 20:59 | 353 | 21 | -42 | 60 | 77 | 684.7 | 73 | -39.7188 | 14.6195
2005-10-13 | 21:59 | 2 | 21.7 | -41.9 | 60 | 79 | 683.9 | 79 | -39.4312 | 15.849
2005-10-13 | 22:59 | 344 | 18.7 | -40 | 62 | 76 | 684 | 75 | -37.6562 | 15.2106
2005-10-13 | 23:59 | 345 | 20.9 | -38.6 | 63 | 76 | 683.4 | 76 | -36.225 | 15.5474
2005-10-14 | 0:59 | 327 | 20.7 | -37.2 | 65 | 74 | 684.2 | 73 | -34.9188 | 15.0511
2005-10-14 | 1:59 | 329 | 18.1 | -36.8 | 65 | 82 | 684.1 | 78 | -34.3625 | 16.1355
2005-10-14 | 2:59 | 328 | 20.6 | -36 | 66 | 80 | 684.2 | 76 | -33.625 | 15.7908
2005-10-14 | 3:59 | 332 | 20.1 | -36.2 | 66 | 73 | 684.2 | 76 | -33.825 | 15.7721
2005-10-14 | 4:59 | 330 | 19.9 | -35.9 | 66 | 75 | 684.6 | 75 | -33.5562 | 15.5894
2005-10-14 | 5:59 | 339 | 18.2 | -35.9 | 66 | 74 | 685 | 72 | -33.65 | 14.9575
2005-10-14 | 6:59 | 328 | 21.8 | -35.6 | 66 | 80 | 684.8 | 76 | -33.225 | 15.8283
2005-10-14 | 7:59 | 333 | 20.2 | -35.5 | 66 | 82 | 684.8 | 78 | -33.0625 | 16.2604
2005-10-14 | 8:59 | 331 | 17.4 | -35.8 | 66 | 85 | 685 | 80 | -33.3 | 16.654
2005-10-14 | 9:59 | 326 | 18.7 | -35.4 | 66 | 84 | 685.2 | 86 | -32.7125 | 17.9652
2005-10-14 | 10:59 | 339 | 17.8 | -35.2 | 67 | 86 | 685.3 | 86 | -32.5125 | 17.9864
2005-10-14 | 11:59 | 315 | 25 | -34.2 | 67 | 84 | 685 | 82 | -31.6375 | 17.2383
2005-10-14 | 12:59 | 312 | 23 | -34.3 | 67 | 83 | 685.2 | 78 | -31.8625 | 16.3757
2005-10-14 | 13:59 | 312 | 25.6 | -33.7 | 68 | 111 | 685.4 | 92 | -30.825 | 19.4326
2005-10-14 | 14:59 | 326 | 22.4 | -33.3 | 68 | 74 | 685.4 | 84 | -30.675 | 17.7583
2005-10-14 | 15:59 | 325 | 25 | -31.9 | 69 | 90 | 685.1 | 78 | -29.4625 | 16.6064
2005-10-14 | 16:59 | 327 | 19.6 | -31.6 | 70 | 76 | 685.6 | 78 | -29.1625 | 16.6352
2005-10-14 | 17:59 | 322 | 26.5 | -31.1 | 70 | 82 | 685.5 | 83 | -28.5063 | 17.7687
2005-10-14 | 18:59 | 319 | 22.1 | -31.8 | 70 | 75 | 686.1 | 75 | -29.4563 | 15.9682
2005-10-14 | 19:59 | 314 | 23.3 | -31.5 | 70 | 79 | 686 | 76 | -29.125 | 16.2122
2005-10-14 | 20:59 | 330 | 20.6 | -32.3 | 69 | 92 | 686.1 | 83 | -29.7063 | 17.646
2005-10-14 | 21:59 | 328 | 21.3 | -32.6 | 69 | 69 | 686 | 103 | -29.3813 | 21.9392
2005-10-14 | 22:59 | 325 | 28.5 | -32.6 | 69 | 76 | 685.4 | 77 | -30.1938 | 16.3241
2005-10-14 | 23:59 | 323 | 25.7 | -32.6 | 69 | 85 | 685.6 | 86 | -29.9125 | 18.2619
2005-10-15 | 0:59 | 323 | 29.2 | -31.8 | 70 | 83 | 685.1 | 86 | -29.1125 | 18.3467
2005-10-15 | 1:59 | 333 | 27.3 | -31.6 | 70 | 82 | 684.6 | 85 | -28.9438 | 18.151
2005-10-15 | 2:59 | 312 | 32.4 | -31.4 | 70 | 86 | 684.1 | 84 | -28.775 | 17.9549
2005-10-15 | 3:59 | 304 | 26.8 | -31.4 | 70 | 84 | 683.7 | 82 | -28.8375 | 17.5211
2005-10-15 | 4:59 | 311 | 30.2 | -31.8 | 70 | 89 | 683.4 | 88 | -29.05 | 18.7801
2005-10-15 | 5:59 | 302 | 33.4 | -31.8 | 70 | 86 | 683.5 | 87 | -29.0813 | 18.5634
2005-10-15 | 6:59 | 302 | 29.3 | -31.9 | 69 | 82 | 683.6 | 81 | -29.3687 | 17.2544
2005-10-15 | 7:59 | 296 | 35.9 | -31.6 | 70 | 86 | 683.1 | 87 | -28.8813 | 18.5848
2005-10-15 | 8:59 | 292 | 35.3 | -32.1 | 69 | 86 | 682.9 | 84 | -29.475 | 17.8825
2005-10-15 | 9:59 | 296 | 30.2 | -31.9 | 70 | 79 | 683.2 | 86 | -29.2125 | 18.3361
2005-10-15 | 10:59 | 297 | 36.9 | -31.4 | 70 | 74 | 682.7 | 78 | -28.9625 | 16.6544
2005-10-15 | 11:59 | 302 | 37.1 | -31.9 | 69 | 84 | 682.6 | 81 | -29.3687 | 17.2544
2005-10-15 | 12:59 | 300 | 34.1 | -31.9 | 70 | 74 | 682.3 | 77 | -29.4937 | 16.3905
2005-10-15 | 13:59 | 295 | 34 | -31.5 | 70 | 80 | 682.7 | 76 | -29.125 | 16.2122
2005-10-15 | 14:59 | 298 | 33.4 | -31.7 | 70 | 91 | 682.7 | 85 | -29.0437 | 18.1405
2005-10-15 | 15:59 | 288 | 32.2 | -31 | 70 | 85 | 683.3 | 84 | -28.375 | 17.9963
2005-10-15 | 16:59 | 287 | 30.5 | -29.7 | 71 | 82 | 684.1 | 86 | -27.0125 | 18.5692
2005-10-15 | 17:59 | 283 | 28.6 | -29.9 | 71 | 79 | 684 | 79 | -27.4312 | 17.017
2005-10-15 | 18:59 | 289 | 26.7 | -30.4 | 71 | 88 | 684.2 | 88 | -27.65 | 18.9319
2005-10-15 | 19:59 | 290 | 27.6 | -30.7 | 70 | 93 | 684.5 | 94 | -27.7625 | 20.2097
2005-10-15 | 20:59 | 295 | 19.6 | -30.5 | 71 | 90 | 684.7 | 91 | -27.6562 | 19.5766
2005-10-15 | 21:59 | 289 | 19.7 | -31.3 | 70 | 99 | 684.6 | 95 | -28.3313 | 20.3581
2005-10-15 | 22:59 | 298 | 22.9 | -31.7 | 70 | 89 | 684.3 | 92 | -28.825 | 19.6593
2005-10-15 | 23:59 | 303 | 28.3 | -32.6 | 69 | 92 | 683.8 | 93 | -29.6938 | 19.7734
2005-10-16 | 0:59 | 302 | 25 | -32.2 | 69 | 100 | 683.8 | 95 | -29.2312 | 20.2528
2005-10-16 | 1:59 | 294 | 26.5 | -32.1 | 69 | 101 | 683.3 | 96 | -29.1 | 20.4815
2005-10-16 | 2:59 | 283 | 24.7 | -30.6 | 71 | 73 | 683.3 | 87 | -27.8813 | 18.692
2005-10-16 | 3:59 | 287 | 18.2 | -30.7 | 70 | 77 | 683.6 | 81 | -28.1687 | 17.3742
2005-10-16 | 4:59 | 284 | 19.8 | -30.5 | 71 | 89 | 683.6 | 87 | -27.7812 | 18.7027
2005-10-16 | 5:59 | 281 | 23.2 | -30.3 | 71 | 91 | 683.3 | 85 | -27.6438 | 18.2871
2005-10-16 | 6:59 | 286 | 20.5 | -30.3 | 71 | 92 | 683.2 | 92 | -27.425 | 19.8179
2005-10-16 | 7:59 | 298 | 23.9 | -30.6 | 71 | 94 | 682.5 | 91 | -27.7563 | 19.5654
2005-10-16 | 8:59 | 295 | 22.1 | -30.6 | 71 | 92 | 682.5 | 91 | -27.7563 | 19.5654
2005-10-16 | 9:59 | 293 | 16.8 | -30.8 | 70 | 94 | 682.3 | 91 | -27.9563 | 19.543
2005-10-16 | 10:59 | 297 | 25.5 | -30.7 | 71 | 94 | 681.5 | 93 | -27.7937 | 19.9911
2005-10-16 | 11:59 | 290 | 27.1 | -30.2 | 71 | 93 | 680.9 | 92 | -27.325 | 19.8293
2005-10-16 | 12:59 | 285 | 26.8 | -29.9 | 71 | 90 | 680.8 | 89 | -27.1187 | 19.2053
2005-10-16 | 13:59 | 289 | 29.7 | -29.9 | 71 | 100 | 680.2 | 95 | -26.9312 | 20.522
2005-10-16 | 14:59 | 278 | 25.9 | -30 | 71 | 103 | 680.8 | 101 | -26.8438 | 21.829
2005-10-16 | 15:59 | 273 | 15.9 | -30.8 | 70 | 136 | 681.6 | 124 | -26.925 | 26.7875
2005-10-16 | 16:59 | 290 | 24.3 | -32 | 69 | 97 | 680.6 | 110 | -28.5625 | 23.5412
2005-10-16 | 17:59 | 290 | 20.2 | -32.5 | 69 | 97 | 680.9 | 97 | -29.4688 | 20.6508
2005-10-16 | 18:59 | 281 | 24 | -32.5 | 69 | 93 | 680.7 | 96 | -29.5 | 20.4342
2005-10-16 | 19:59 | 288 | 20.6 | -32.7 | 69 | 109 | 680.7 | 112 | -29.2 | 23.8813
2005-10-16 | 20:59 | 292 | 14.3 | -32.5 | 69 | 194 | 681.1 | 131 | -28.4062 | 28.0607
2005-10-16 | 21:59 | 294 | 14.5 | -33.7 | 68 | 125 | 680.7 | 129 | -29.6687 | 27.4316
2005-10-16 | 22:59 | 295 | 16.9 | -34.1 | 68 | 131 | 680.5 | 121 | -30.3188 | 25.6335
2005-10-16 | 23:59 | 294 | 18 | -33.6 | 68 | 119 | 680.2 | 125 | -29.6938 | 26.5772
2005-10-17 | 0:59 | 295 | 21.3 | -32.7 | 69 | 101 | 680.5 | 110 | -29.2625 | 23.4463
2005-10-17 | 1:59 | 306 | 18.1 | -32.7 | 69 | 96 | 680.4 | 98 | -29.6375 | 20.8433
2005-10-17 | 2:59 | 303 | 16 | -32.4 | 69 | 85 | 680.4 | 91 | -29.5562 | 19.3636
2005-10-17 | 3:59 | 313 | 17.6 | -32.2 | 69 | 85 | 680.2 | 84 | -29.575 | 17.8721
2005-10-17 | 4:59 | 307 | 12.5 | -32.2 | 69 | 104 | 680.4 | 94 | -29.2625 | 20.036
2005-10-17 | 5:59 | 312 | 13.8 | -32.4 | 69 | 97 | 680.3 | 100 | -29.275 | 21.3133
2005-10-17 | 6:59 | 307 | 14.2 | -32.7 | 69 | 94 | 680.2 | 96 | -29.7 | 20.4105
2005-10-17 | 7:59 | 300 | 15.7 | -33.3 | 68 | 102 | 679.9 | 97 | -30.2688 | 20.5552
2005-10-17 | 8:59 | 305 | 12.2 | -33.7 | 68 | 133 | 680.3 | 105 | -30.4187 | 22.231
2005-10-17 | 9:59 | 314 | 11.2 | -35.7 | 67 | 133 | 680.5 | 130 | -31.6375 | 27.3289
2005-10-17 | 10:59 | 313 | 10.5 | -37.2 | 66 | 145 | 680.5 | 127 | -33.2313 | 26.4489
2005-10-17 | 11:59 | 313 | 10.8 | -36.1 | 66 | 108 | 680.8 | 128 | -32.1 | 26.8356
2005-10-17 | 12:59 | 316 | 12.5 | -37.3 | 65 | 133 | 680.8 | 130 | -33.2375 | 27.0727
2005-10-17 | 13:59 | 310 | 11.5 | -37.2 | 65 | 111 | 680.9 | 124 | -33.325 | 25.8098
2005-10-17 | 14:59 | 301 | 12.6 | -35.4 | 67 | 90 | 680.9 | 99 | -32.3062 | 20.7305
2005-10-17 | 15:59 | 313 | 11.7 | -34.5 | 67 | 106 | 681.4 | 102 | -31.3125 | 21.4835
2005-10-17 | 16:59 | 306 | 12.1 | -34.2 | 68 | 111 | 681.6 | 113 | -30.6687 | 23.89
2005-10-17 | 17:59 | 310 | 11 | -34.5 | 67 | 99 | 681.8 | 91 | -31.6562 | 19.1282
2005-10-17 | 18:59 | 304 | 12.2 | -34.7 | 67 | 130 | 682 | 114 | -31.1375 | 24.0356
2005-10-17 | 19:59 | 301 | 11.5 | -34.4 | 67 | 102 | 682.2 | 108 | -31.025 | 22.7855
2005-10-17 | 20:59 | 317 | 8.1 | -34.5 | 67 | 95 | 682.7 | 106 | -31.1875 | 22.3424
2005-10-17 | 21:59 | 311 | 9.5 | -35 | 67 | 107 | 682.5 | 109 | -31.5938 | 22.9201
2005-10-17 | 22:59 | 328 | 10.4 | -35.2 | 67 | 119 | 682.7 | 117 | -31.5437 | 24.6096
2005-10-17 | 23:59 | 318 | 8.8 | -34.7 | 67 | 124 | 682.9 | 113 | -31.1687 | 23.8204
2005-10-18 | 0:59 | 306 | 9 | -33.8 | 68 | 121 | 682.8 | 116 | -30.175 | 24.5948
2005-10-18 | 1:59 | 334 | 7.1 | -33.4 | 68 | 94 | 682.6 | 109 | -29.9937 | 23.135
2005-10-18 | 2:59 | 313 | 9.9 | -32.5 | 69 | 96 | 682.7 | 103 | -29.2812 | 21.9519
2005-10-18 | 3:59 | 302 | 10.9 | -33.1 | 68 | 76 | 682.9 | 84 | -30.475 | 17.779
2005-10-18 | 4:59 | 313 | 9.5 | -33.4 | 68 | 104 | 683.1 | 83 | -30.8062 | 17.5335
2005-10-18 | 5:59 | 325 | 8 | -33.6 | 68 | 105 | 683 | 97 | -30.5688 | 20.5193
2005-10-18 | 6:59 | 313 | 8.1 | -34 | 67 | 135 | 683.3 | 117 | -30.3438 | 24.7825
2005-10-18 | 7:59 | 324 | 8.1 | -34.1 | 67 | 124 | 683 | 136 | -29.85 | 28.8898
2005-10-18 | 8:59 | 330 | 8.9 | -33.6 | 68 | 104 | 682.9 | 118 | -29.9125 | 25.057
2005-10-18 | 9:59 | 338 | 8.6 | -34.4 | 67 | 136 | 683 | 119 | -30.6812 | 25.1567
2005-10-18 | 10:59 | 332 | 9 | -35.7 | 66 | 116 | 683 | 144 | -31.2 | 30.3497
2005-10-18 | 11:59 | 340 | 9.8 | -37.5 | 66 | 123 | 683.2 | 111 | -34.0312 | 23.0074
2005-10-18 | 12:59 | 334 | 10 | -37.9 | 65 | 147 | 683.2 | 137 | -33.6187 | 28.4661
2005-10-18 | 13:59 | 352 | 10.2 | -39.1 | 64 | 106 | 683.3 | 116 | -35.475 | 23.8374
2005-10-18 | 14:59 | 5 | 12.7 | -40.7 | 63 | 139 | 683.3 | 121 | -36.9188 | 24.6496
2005-10-18 | 15:59 | 0 | 9.9 | -40.9 | 62 | 156 | 683.6 | 162 | -35.8375 | 33.2178
2005-10-18 | 16:59 | 0 | 10.7 | -41.3 | 62 | 163 | 683.6 | 158 | -36.3625 | 32.2954
2005-10-18 | 17:59 | 8 | 14.2 | -41.1 | 62 | 166 | 683.5 | 163 | -36.0063 | 33.389
2005-10-18 | 18:59 | 1 | 8.5 | -41.9 | 61 | 194 | 683.9 | 127 | -37.9312 | 25.7135
2005-10-18 | 19:59 | 357 | 8.3 | -42.4 | 61 | 77 | 684.1 | 138 | -38.0875 | 27.9141
2005-10-18 | 20:59 | 7 | 9.5 | -41.8 | 61 | 97 | 684.2 | 89 | -39.0187 | 17.9005
2005-10-18 | 21:59 | 7 | 9.3 | -41.1 | 62 | 107 | 684.3 | 104 | -37.85 | 21.0672
2005-10-18 | 22:59 | 10 | 9.6 | -41.5 | 61 | 80 | 684.2 | 93 | -38.5938 | 18.7537
2005-10-18 | 23:59 | 7 | 13 | -42.1 | 61 | 111 | 684.3 | 92 | -39.225 | 18.4805
2005-10-19 | 0:59 | 352 | 10.8 | -42.4 | 60 | 133 | 684.5 | 136 | -38.15 | 27.4991
2005-10-19 | 1:59 | 1 | 9.8 | -42.7 | 60 | 144 | 684.5 | 136 | -38.45 | 27.4488
2005-10-19 | 2:59 | 24 | 6.5 | -42.9 | 60 | 107 | 684.5 | 135 | -38.6812 | 27.2085
2005-10-19 | 3:59 | 16 | 6.9 | -42.8 | 60 | 107 | 684.6 | 98 | -39.7375 | 19.6239
2005-10-19 | 4:59 | 22 | 9 | -42.8 | 60 | 179 | 684.7 | 156 | -37.925 | 31.5863
2005-10-19 | 5:59 | 16 | 12.6 | -42.3 | 60 | 199 | 684.7 | 186 | -36.4875 | 37.99
2005-10-19 | 6:59 | 7 | 10.4 | -42 | 60 | 132 | 684.8 | 185 | -36.2188 | 37.847
2005-10-19 | 7:59 | 3 | 10.7 | -42 | 61 | 115 | 684.8 | 120 | -38.25 | 24.2491
2005-10-19 | 8:59 | 13 | 9.2 | -41.8 | 61 | 127 | 684.8 | 128 | -37.8 | 25.9367
2005-10-19 | 9:59 | 35 | 7.6 | -41 | 61 | 132 | 685.1 | 125 | -37.0938 | 25.4376
2005-10-19 | 10:59 | 17 | 8.6 | -40.8 | 62 | 115 | 685 | 126 | -36.8625 | 25.677
2005-10-19 | 11:59 | 23 | 7.6 | -40.3 | 62 | 115 | 685.2 | 106 | -36.9875 | 21.5849
2005-10-19 | 12:59 | 20 | 7.5 | -39.3 | 62 | 113 | 685.2 | 120 | -35.55 | 24.6483
2005-10-19 | 13:59 | 14 | 9.3 | -39.1 | 62 | 112 | 685.2 | 113 | -35.5688 | 23.2079
2005-10-19 | 14:59 | 24 | 7.1 | -39.4 | 61 | 140 | 685.2 | 126 | -35.4625 | 25.8943
2005-10-19 | 15:59 | 35 | 5.9 | -39.8 | 60 | 129 | 685.3 | 134 | -35.6125 | 27.5136
2005-10-19 | 16:59 | 46 | 5.5 | -40.1 | 59 | 123 | 685.3 | 128 | -36.1 | 26.2048
2005-10-19 | 17:59 | 46 | 7.6 | -40.4 | 58 | 123 | 685.5 | 122 | -36.5875 | 24.9032
2005-10-19 | 18:59 | 52 | 9 | -41 | 56 | 122 | 685.7 | 117 | -37.3438 | 23.7735
2005-10-19 | 19:59 | 55 | 8.8 | -41.4 | 55 | 114 | 685.8 | 121 | -37.6187 | 24.5453
2005-10-19 | 20:59 | 36 | 11.1 | -41.8 | 55 | 135 | 685.6 | 125 | -37.8937 | 25.3144
2005-10-19 | 21:59 | 40 | 8 | -42.6 | 54 | 155 | 685.9 | 143 | -38.1313 | 28.9178
2005-10-19 | 22:59 | 42 | 10.7 | -43 | 54 | 145 | 686 | 148 | -38.375 | 29.8845
2005-10-19 | 23:59 | 41 | 9.7 | -43.2 | 55 | 172 | 686 | 153 | -38.4188 | 30.8858
2005-10-20 | 0:59 | 47 | 8.5 | -43.9 | 54 | 151 | 686.2 | 176 | -38.4 | 35.5329
2005-10-20 | 1:59 | 56 | 7.3 | -45.8 | 54 | 190 | 686.4 | 165 | -40.6437 | 32.8559
2005-10-20 | 2:59 | 43 | 10.9 | -44.7 | 54 | 196 | 686.3 | 191 | -38.7313 | 38.4833
2005-10-20 | 3:59 | 64 | 8.7 | -46.6 | 53 | 192 | 686.3 | 198 | -40.4125 | 39.4835
2005-10-20 | 4:59 | 48 | 10.2 | -46.6 | 53 | 163 | 686.4 | 173 | -41.1938 | 34.3317
2005-10-20 | 5:59 | 44 | 12.9 | -45.6 | 54 | 172 | 686.4 | 137 | -41.3188 | 27.1665
2005-10-20 | 6:59 | 64 | 8.5 | -48.6 | 52 | 157 | 686.7 | 174 | -43.1625 | 34.1081
2005-10-20 | 7:59 | 63 | 7.4 | -47.3 | 53 | 188 | 686.8 | 184 | -41.55 | 36.4339
2005-10-20 | 8:59 | 57 | 12.5 | -47.2 | 54 | 182 | 686.8 | 191 | -41.2313 | 37.895
2005-10-20 | 9:59 | 72 | 6.8 | -48.1 | 53 | 172 | 686.8 | 175 | -42.6313 | 34.4187
2005-10-20 | 10:59 | 56 | 11 | -46 | 55 | 204 | 686.8 | 183 | -40.2812 | 36.522
2005-10-20 | 11:59 | 63 | 9.6 | -47.1 | 54 | 185 | 686.7 | 195 | -41.0063 | 38.7427
2005-10-20 | 12:59 | 64 | 9.5 | -46.9 | 54 | 194 | 686.6 | 198 | -40.7125 | 39.4104
2005-10-20 | 13:59 | 63 | 10.1 | -46.8 | 54 | 207 | 686.6 | 198 | -40.6125 | 39.4347
2005-10-20 | 14:59 | 57 | 11.6 | -47.5 | 53 | 190 | 686.3 | 194 | -41.4375 | 38.4409
2005-10-20 | 15:59 | 57 | 14.1 | -47.6 | 53 | 175 | 686.3 | 186 | -41.7875 | 36.7755
2005-10-20 | 16:59 | 57 | 12.1 | -48.5 | 52 | 200 | 686.3 | 187 | -42.6562 | 36.7731
2005-10-20 | 17:59 | 63 | 10.6 | -48.8 | 52 | 191 | 686.5 | 192 | -42.8 | 37.7223
2005-10-20 | 18:59 | 70 | 11.6 | -49.3 | 52 | 191 | 686.2 | 188 | -43.425 | 36.7917
2005-10-20 | 19:59 | 72 | 11.3 | -49.5 | 52 | 100 | 686.3 | 187 | -43.6562 | 36.5427
2005-10-20 | 20:59 | 68 | 11.3 | -49.6 | 52 | 190 | 686.2 | 188 | -43.725 | 36.7222
2005-10-20 | 21:59 | 67 | 10.1 | -49.6 | 52 | 195 | 686.3 | 192 | -43.6 | 37.5331
2005-10-20 | 22:59 | 78 | 10.8 | -50 | 51 | 199 | 686.1 | 197 | -43.8438 | 38.4513
2005-10-20 | 23:59 | 73 | 10 | -50.5 | 50 | 204 | 686 | 201 | -44.2188 | 39.1392
2005-10-21 | 0:59 | 75 | 10.7 | -50.8 | 50 | 210 | 685.7 | 207 | -44.3312 | 40.2789
2005-10-21 | 1:59 | 69 | 11.6 | -50.8 | 50 | 215 | 685.3 | 213 | -44.1437 | 41.4956
2005-10-21 | 2:59 | 69 | 9.6 | -50.7 | 50 | 219 | 685.3 | 217 | -43.9188 | 42.335
2005-10-21 | 3:59 | 61 | 10.8 | -50.3 | 50 | 222 | 684.9 | 219 | -43.4562 | 42.85
2005-10-21 | 4:59 | 73 | 12.4 | -51 | 50 | 220 | 684.7 | 214 | -44.3125 | 41.6459
2005-10-21 | 5:59 | 73 | 10.4 | -51.4 | 49 | 226 | 684.7 | 166 | -46.2125 | 31.9162
2005-10-21 | 6:59 | 65 | 11.3 | -51.4 | 49 | 229 | 684.6 | 228 | -44.275 | 44.3809
2005-10-21 | 7:59 | 76 | 9.2 | -52 | 48 | 227 | 684.5 | 228 | -44.875 | 44.2124
2005-10-21 | 8:59 | 70 | 10.9 | -52.4 | 48 | 226 | 684.3 | 225 | -45.3687 | 43.4938
2005-10-21 | 9:59 | 73 | 10.5 | -52.5 | 48 | 223 | 684 | 224 | -45.5 | 43.2643
2005-10-21 | 10:59 | 67 | 10.7 | -52.1 | 48 | 218 | 684 | 221 | -45.1938 | 42.7682
2005-10-21 | 11:59 | 63 | 10.6 | -52.3 | 48 | 213 | 684.1 | 216 | -45.55 | 41.7058
2005-10-21 | 12:59 | 72 | 10.8 | -52.7 | 47 | 208 | 684 | 210 | -46.1375 | 40.3953
2005-10-21 | 13:59 | 67 | 10.8 | -53.1 | 47 | 204 | 683.9 | 206 | -46.6625 | 39.4926
2005-10-21 | 14:59 | 64 | 10.6 | -53 | 47 | 200 | 683.9 | 202 | -46.6875 | 38.7196
2005-10-21 | 15:59 | 71 | 9.2 | -53.5 | 47 | 196 | 684 | 198 | -47.3125 | 37.8004
2005-10-21 | 16:59 | 69 | 10.7 | -53.8 | 46 | 195 | 684 | 196 | -47.675 | 37.331
2005-10-21 | 17:59 | 60 | 11.3 | -53.7 | 46 | 196 | 684.1 | 195 | -47.6063 | 37.1571
2005-10-21 | 18:59 | 57 | 10.4 | -53.9 | 46 | 198 | 684 | 197 | -47.7437 | 37.5048
2005-10-21 | 19:59 | 59 | 8.5 | -54.2 | 46 | 118 | 684.3 | 195 | -48.1063 | 37.037
2005-10-21 | 20:59 | 58 | 8 | -54.6 | 46 | 200 | 684.6 | 197 | -48.4438 | 37.3349
2005-10-21 | 21:59 | 50 | 11 | -54.7 | 46 | 203 | 684.9 | 201 | -48.4188 | 38.0992
2005-10-21 | 22:59 | 45 | 9 | -54.8 | 45 | 191 | 685.1 | 197 | -48.6437 | 37.2864
2005-10-21 | 23:59 | 51 | 7.9 | -54.3 | 46 | 221 | 685.2 | 211 | -47.7062 | 40.1799
2005-10-22 | 0:59 | 40 | 9.3 | -53.2 | 47 | 224 | 685.4 | 219 | -46.3563 | 42.0675
2005-10-22 | 1:59 | 50 | 8.5 | -54.3 | 46 | 233 | 685.6 | 205 | -47.8937 | 38.99
2005-10-22 | 2:59 | 50 | 8.2 | -54.8 | 45 | 135 | 686 | 202 | -48.4875 | 38.2716
2005-10-22 | 3:59 | 54 | 7.9 | -54.7 | 45 | 241 | 686.1 | 202 | -48.3875 | 38.2965
2005-10-22 | 4:59 | 42 | 9.2 | -53.5 | 46 | 148 | 686.5 | 222 | -46.5625 | 42.5874
2005-10-22 | 5:59 | 48 | 9.5 | -52.8 | 47 | 170 | 686.7 | 163 | -47.7062 | 31.0394
2005-10-22 | 6:59 | 43 | 9.5 | -52.6 | 47 | 108 | 687.2 | 206 | -46.1625 | 39.6195
2005-10-22 | 7:59 | 49 | 8.4 | -52.8 | 47 | 231 | 687.5 | 219 | -45.9562 | 42.1754
2005-10-22 | 8:59 | 39 | 9.5 | -51.8 | 47 | 152 | 687.5 | 235 | -44.4562 | 45.691
2005-10-22 | 9:59 | 40 | 10.4 | -51.8 | 47 | 241 | 688 | 185 | -46.0187 | 35.6134
2005-10-22 | 10:59 | 33 | 11.1 | -51.5 | 48 | 271 | 688.2 | 208 | -45 | 40.3021
2005-10-22 | 11:59 | 36 | 9 | -51.3 | 48 | 153 | 688.6 | 226 | -44.2375 | 44.0021
2005-10-22 | 12:59 | 39 | 8.5 | -51.4 | 48 | 187 | 688.9 | 169 | -46.1187 | 32.5125
2005-10-22 | 13:59 | 45 | 10.9 | -51.1 | 48 | 165 | 688.8 | 179 | -45.5063 | 34.5714
2005-10-22 | 14:59 | 43 | 8.6 | -50.7 | 49 | 188 | 689.1 | 183 | -44.9813 | 35.4623
2005-10-22 | 15:59 | 48 | 7.9 | -50.6 | 49 | 190 | 689.2 | 189 | -44.6938 | 36.6919
2005-10-22 | 16:59 | 41 | 10.8 | -50.7 | 49 | 197 | 689.2 | 183 | -44.9813 | 35.4623
2005-10-22 | 17:59 | 61 | 9 | -52.2 | 47 | 205 | 689.4 | 197 | -46.0438 | 37.9174
2005-10-22 | 18:59 | 59 | 9 | -52.7 | 47 | 168 | 689.4 | 170 | -47.3875 | 32.4392
2005-10-22 | 19:59 | 71 | 9.1 | -53.3 | 47 | 147 | 689.7 | 191 | -47.3312 | 36.4596
2005-10-22 | 20:59 | 71 | 9.2 | -53.6 | 47 | 206 | 689.5 | 202 | -47.2875 | 38.5702
2005-10-22 | 21:59 | 81 | 9.3 | -53.7 | 46 | 211 | 689.4 | 208 | -47.2 | 39.7383
2005-10-22 | 22:59 | 75 | 10.7 | -53 | 47 | 215 | 689.2 | 213 | -46.3438 | 40.9183
2005-10-22 | 23:59 | 81 | 10.5 | -53 | 47 | 221 | 688.9 | 218 | -46.1875 | 41.9207
2005-10-23 | 0:59 | 87 | 6.7 | -52.4 | 47 | 226 | 688.7 | 224 | -45.4 | 43.2919
2005-10-23 | 1:59 | 97 | 10.8 | -52.8 | 47 | 230 | 688.4 | 228 | -45.675 | 43.9877
2005-10-23 | 2:59 | 97 | 9 | -52.9 | 47 | 236 | 688.1 | 233 | -45.6187 | 44.9685
2005-10-23 | 3:59 | 94 | 11.4 | -52.9 | 47 | 240 | 687.7 | 237 | -45.4937 | 45.777
2005-10-23 | 4:59 | 87 | 11.7 | -52.7 | 47 | 239 | 687.3 | 233 | -45.4188 | 45.0259
2005-10-23 | 5:59 | 83 | 11.9 | -52.6 | 47 | 244 | 687.1 | 174 | -47.1625 | 33.2507
2005-10-23 | 6:59 | 81 | 10.1 | -52.7 | 47 | 243 | 686.6 | 243 | -45.1063 | 47.0519
2005-10-23 | 7:59 | 71 | 7.7 | -51.2 | 48 | 241 | 686.3 | 242 | -43.6375 | 47.2961
2005-10-23 | 8:59 | 79 | 10.4 | -51.5 | 48 | 237 | 685.8 | 237 | -44.0938 | 46.1857
2005-10-23 | 9:59 | 88 | 10.3 | -51.6 | 48 | 232 | 685.6 | 235 | -44.2563 | 45.7489
2005-10-23 | 10:59 | 80 | 11.9 | -52 | 47 | 230 | 685 | 230 | -44.8125 | 44.6179
2005-10-23 | 11:59 | 90 | 12.5 | -51.7 | 48 | 224 | 684.6 | 227 | -44.6063 | 44.0936
2005-10-23 | 12:59 | 86 | 11.5 | -51.8 | 48 | 221 | 684.2 | 222 | -44.8625 | 43.0523
2005-10-23 | 13:59 | 84 | 12.9 | -51.3 | 48 | 216 | 683.7 | 218 | -44.4875 | 42.3773
2005-10-23 | 14:59 | 93 | 12.9 | -50.9 | 49 | 212 | 683.4 | 214 | -44.2125 | 41.6723
2005-10-23 | 15:59 | 82 | 10.7 | -51.7 | 48 | 208 | 683 | 210 | -45.1375 | 40.654
2005-10-23 | 16:59 | 81 | 12 | -51.8 | 48 | 206 | 682.7 | 208 | -45.3 | 40.2252
2005-10-23 | 17:59 | 78 | 11.9 | -52 | 48 | 207 | 682.4 | 206 | -45.5625 | 39.7718
2005-10-23 | 18:59 | 80 | 13.1 | -51.2 | 49 | 208 | 682.2 | 209 | -44.6688 | 40.5811
2005-10-23 | 19:59 | 80 | 11.5 | -51.6 | 48 | 189 | 681.9 | 206 | -45.1625 | 39.8733
2005-10-23 | 20:59 | 77 | 12.3 | -51.2 | 49 | 209 | 681.6 | 205 | -44.7938 | 39.7729
2005-10-23 | 21:59 | 77 | 12.5 | -51.6 | 49 | 214 | 681.3 | 210 | -45.0375 | 40.6799
2005-10-23 | 22:59 | 77 | 11.3 | -51.6 | 49 | 218 | 681.1 | 216 | -44.85 | 41.8921
2005-10-23 | 23:59 | 67 | 15.1 | -50.4 | 50 | 224 | 680.8 | 221 | -43.4937 | 43.2311
2005-10-24 | 0:59 | 75 | 14.1 | -50.2 | 50 | 223 | 680.5 | 227 | -43.1063 | 44.5131
2005-10-24 | 1:59 | 69 | 12.3 | -50.9 | 49 | 234 | 680.3 | 232 | -43.65 | 45.3382
2005-10-24 | 2:59 | 72 | 11.2 | -51.5 | 48 | 238 | 680 | 235 | -44.1562 | 45.7779
2005-10-24 | 3:59 | 68 | 11.2 | -51.8 | 48 | 241 | 679.8 | 238 | -44.3625 | 46.3018
2005-10-24 | 4:59 | 61 | 13.2 | -51.8 | 48 | 234 | 679.6 | 235 | -44.4562 | 45.691
2005-10-24 | 5:59 | 54 | 12.2 | -51.9 | 48 | 248 | 679.8 | 178 | -46.3375 | 34.196
2005-10-24 | 6:59 | 46 | 11.1 | -51.6 | 48 | 242 | 680 | 240 | -44.1 | 46.7685
2005-10-24 | 7:59 | 46 | 13.2 | -51.3 | 48 | 239 | 679.7 | 243 | -43.7062 | 47.471
2005-10-24 | 8:59 | 45 | 13.9 | -51.1 | 48 | 248 | 679.7 | 237 | -43.6938 | 46.3025
2005-10-24 | 9:59 | 42 | 14.4 | -50.7 | 49 | 227 | 679.5 | 239 | -43.2313 | 46.8294
2005-10-24 | 10:59 | 36 | 13.4 | -50.6 | 49 | 236 | 679.6 | 233 | -43.3188 | 45.6287
2005-10-24 | 11:59 | 38 | 13.5 | -50.5 | 49 | 232 | 679.4 | 234 | -43.1875 | 45.8624
2005-10-24 | 12:59 | 40 | 13.1 | -50.7 | 49 | 228 | 679.6 | 229 | -43.5438 | 44.7819
2005-10-24 | 13:59 | 34 | 14 | -50.3 | 49 | 191 | 679.5 | 218 | -43.4875 | 42.6459
2005-10-24 | 14:59 | 37 | 16.3 | -50.1 | 49 | 219 | 679.3 | 216 | -43.35 | 42.2912
2005-10-24 | 15:59 | 37 | 14.9 | -49.9 | 50 | 215 | 679.7 | 208 | -43.4 | 40.7121
2005-10-24 | 16:59 | 34 | 15.7 | -49.8 | 50 | 213 | 679.4 | 211 | -43.2062 | 41.3496
2005-10-24 | 17:59 | 28 | 13 | -49.6 | 50 | 213 | 679.9 | 215 | -42.8813 | 42.2196
2005-10-24 | 18:59 | 37 | 13.9 | -49.9 | 50 | 214 | 680.1 | 212 | -43.275 | 41.5277
2005-10-24 | 19:59 | 45 | 11.2 | -50.3 | 50 | 212 | 680.3 | 216 | -43.55 | 42.238
2005-10-24 | 20:59 | 50 | 9.3 | -51 | 49 | 219 | 680.6 | 214 | -44.3125 | 41.6459
2005-10-24 | 21:59 | 43 | 9.7 | -51.3 | 49 | 224 | 680.8 | 222 | -44.3625 | 43.1891
2005-10-24 | 22:59 | 53 | 7.2 | -53.4 | 47 | 220 | 681.2 | 226 | -46.3375 | 43.4174
2005-10-24 | 23:59 | 50 | 8.9 | -53.1 | 47 | 236 | 681.2 | 232 | -45.85 | 44.7094
2005-10-25 | 0:59 | 48 | 8.4 | -53.3 | 47 | 241 | 681.2 | 239 | -45.8312 | 46.0639
2005-10-25 | 1:59 | 52 | 9 | -53 | 48 | 248 | 681.5 | 245 | -45.3438 | 47.3674
2005-10-25 | 2:59 | 60 | 9.9 | -52.9 | 48 | 254 | 681.7 | 251 | -45.0562 | 48.6164
2005-10-25 | 3:59 | 64 | 12.2 | -52.5 | 48 | 257 | 682 | 254 | -44.5625 | 49.3519
2005-10-25 | 4:59 | 81 | 6.9 | -52.9 | 48 | 256 | 682.4 | 244 | -45.275 | 47.1948
2005-10-25 | 5:59 | 69 | 11.2 | -53 | 48 | 260 | 682.5 | 189 | -47.0938 | 36.1331
2005-10-25 | 6:59 | 70 | 10.5 | -52.6 | 48 | 261 | 682.5 | 261 | -44.4438 | 50.7502
2005-10-25 | 7:59 | 72 | 10.6 | -52.6 | 48 | 259 | 682.5 | 260 | -44.475 | 50.5458
2005-10-25 | 8:59 | 71 | 8.7 | -53 | 47 | 257 | 682.8 | 256 | -45 | 49.6026
2005-10-25 | 9:59 | 80 | 10.1 | -52.7 | 47 | 252 | 682.9 | 254 | -44.7625 | 49.2894
2005-10-25 | 10:59 | 86 | 8.5 | -52.5 | 48 | 246 | 683 | 249 | -44.7188 | 48.3325
2005-10-25 | 11:59 | 89 | 10.4 | -52.2 | 48 | 241 | 683.1 | 242 | -44.6375 | 46.998
2005-10-25 | 12:59 | 76 | 10.3 | -51.7 | 48 | 234 | 683 | 238 | -44.2625 | 46.3311
2005-10-25 | 13:59 | 80 | 10.3 | -51.2 | 49 | 230 | 682.8 | 232 | -43.95 | 45.2524
2005-10-25 | 14:59 | 69 | 14.7 | -50.5 | 50 | 227 | 682.6 | 228 | -43.375 | 44.6337
2005-10-25 | 15:59 | 79 | 11.6 | -50.1 | 50 | 222 | 682.7 | 224 | -43.1 | 43.9266
2005-10-25 | 16:59 | 77 | 12.9 | -50.6 | 50 | 220 | 682.6 | 221 | -43.6938 | 43.1766
2005-10-25 | 17:59 | 79 | 12.5 | -50 | 50 | 220 | 682.5 | 220 | -43.125 | 43.1354
2005-10-25 | 18:59 | 79 | 11.8 | -50.2 | 50 | 221 | 682.5 | 221 | -43.2938 | 43.2855
2005-10-25 | 19:59 | 68 | 13.4 | -50 | 50 | 220 | 682.3 | 220 | -43.125 | 43.1354
2005-10-25 | 20:59 | 74 | 12.5 | -49.5 | 51 | 224 | 682.1 | 219 | -42.6562 | 43.0658
2005-10-25 | 21:59 | 65 | 14.2 | -49.3 | 51 | 225 | 682 | 225 | -42.2687 | 44.3531
2005-10-25 | 22:59 | 67 | 12.6 | -48.5 | 52 | 231 | 682 | 229 | -41.3438 | 45.4026
2005-10-25 | 23:59 | 61 | 14 | -47.8 | 52 | 239 | 681.9 | 235 | -40.4562 | 46.8491
2005-10-26 | 0:59 | 64 | 11.5 | -47.8 | 52 | 249 | 682 | 243 | -40.2062 | 48.5188
2005-10-26 | 1:59 | 66 | 10.9 | -47.5 | 52 | 271 | 682 | 254 | -39.5625 | 50.9166
2005-10-26 | 2:59 | 58 | 13.7 | -47.3 | 52 | 251 | 681.8 | 241 | -39.7687 | 48.2494
2005-10-26 | 3:59 | 58 | 13.5 | -47.7 | 52 | 237 | 682 | 239 | -40.2313 | 47.7128
2005-10-26 | 4:59 | 64 | 13.2 | -48 | 52 | 272 | 682.3 | 255 | -40.0312 | 50.9698
2005-10-26 | 5:59 | 55 | 14.4 | -48.1 | 52 | 268 | 682.1 | 194 | -42.0375 | 38.2975
2005-10-26 | 6:59 | 58 | 13.4 | -48.3 | 52 | 267 | 682.1 | 263 | -40.0812 | 52.5526
2005-10-26 | 7:59 | 52 | 11.5 | -47.3 | 52 | 261 | 682.3 | 263 | -39.0812 | 52.8766
2005-10-26 | 8:59 | 59 | 12.7 | -47.6 | 52 | 261 | 682.5 | 259 | -39.5063 | 51.9368
2005-10-26 | 9:59 | 61 | 12.6 | -48.3 | 51 | 256 | 682.6 | 258 | -40.2375 | 51.5039
2005-10-26 | 10:59 | 60 | 13.3 | -48.7 | 51 | 252 | 682.5 | 254 | -40.7625 | 50.5411
2005-10-26 | 11:59 | 55 | 14.8 | -48.5 | 51 | 247 | 682.8 | 249 | -40.7188 | 49.5596
2005-10-26 | 12:59 | 64 | 10.2 | -48.1 | 52 | 241 | 683 | 244 | -40.475 | 48.6377
2005-10-26 | 13:59 | 59 | 12.6 | -48.7 | 51 | 237 | 683 | 239 | -41.2313 | 47.4183
2005-10-26 | 14:59 | 66 | 11.4 | -49.7 | 50 | 233 | 683 | 235 | -42.3563 | 46.299
2005-10-26 | 15:59 | 60 | 10.6 | -48.4 | 51 | 230 | 683 | 232 | -41.15 | 46.0527
2005-10-26 | 16:59 | 67 | 11.6 | -49.1 | 51 | 228 | 683 | 229 | -41.9438 | 45.2333
2005-10-26 | 17:59 | 64 | 12.5 | -49.8 | 51 | 228 | 683.4 | 228 | -42.675 | 44.8304
2005-10-26 | 18:59 | 58 | 12.8 | -49.6 | 51 | 230 | 683.5 | 230 | -42.4125 | 45.298
2005-10-26 | 19:59 | 66 | 11.5 | -49.5 | 51 | 230 | 683.5 | 230 | -42.3125 | 45.3263
2005-10-26 | 20:59 | 71 | 10.6 | -50.1 | 50 | 233 | 683.6 | 228 | -42.975 | 44.7461
2005-10-26 | 21:59 | 67 | 12.4 | -50.2 | 50 | 238 | 683.6 | 235 | -42.8563 | 46.1543
2005-10-26 | 22:59 | 60 | 12.8 | -49.7 | 50 | 243 | 683.8 | 240 | -42.2 | 47.3303
2005-10-26 | 23:59 | 60 | 11.9 | -49.8 | 50 | 249 | 683.7 | 246 | -42.1125 | 48.5401
2005-10-27 | 0:59 | 61 | 9.7 | -49.7 | 50 | 255 | 683.7 | 252 | -41.825 | 49.8132
2005-10-27 | 1:59 | 62 | 10.6 | -49.6 | 50 | 261 | 683.6 | 258 | -41.5375 | 51.0907
2005-10-27 | 2:59 | 63 | 9.6 | -50.2 | 50 | 265 | 683.5 | 263 | -41.9813 | 51.937
2005-10-27 | 3:59 | 62 | 9.7 | -50.4 | 50 | 269 | 683.5 | 265 | -42.1187 | 52.2871
2005-10-27 | 4:59 | 57 | 9.7 | -50.1 | 50 | 268 | 683.4 | 258 | -42.0375 | 50.9317
2005-10-27 | 5:59 | 67 | 8.9 | -50.3 | 49 | 273 | 683.9 | 194 | -44.2375 | 37.7717
2005-10-27 | 6:59 | 65 | 10.8 | -51.1 | 49 | 274 | 683.8 | 274 | -42.5375 | 53.9215
2005-10-27 | 7:59 | 60 | 10.1 | -50.1 | 49 | 272 | 683.6 | 273 | -41.5688 | 54.0505
2005-10-27 | 8:59 | 71 | 9.2 | -50.7 | 49 | 268 | 683.5 | 268 | -42.325 | 52.8109
2005-10-27 | 9:59 | 58 | 14 | -50.1 | 49 | 264 | 683 | 266 | -41.7875 | 52.5929
2005-10-27 | 10:59 | 57 | 12 | -49.7 | 50 | 259 | 682.8 | 262 | -41.5125 | 51.8908
2005-10-27 | 11:59 | 55 | 11.8 | -50.1 | 49 | 252 | 683.1 | 255 | -42.1313 | 50.31
2005-10-27 | 12:59 | 42 | 9.8 | -48.6 | 51 | 248 | 683 | 250 | -40.7875 | 49.7375
2005-10-27 | 13:59 | 42 | 12.6 | -48.7 | 51 | 242 | 682.9 | 245 | -41.0438 | 48.6654
2005-10-27 | 14:59 | 36 | 11.3 | -47.6 | 52 | 238 | 682.7 | 240 | -40.1 | 47.9512
2005-10-27 | 15:59 | 32 | 12.5 | -47.6 | 52 | 235 | 682.6 | 237 | -40.1938 | 47.3245
2005-10-27 | 16:59 | 35 | 13.3 | -47.4 | 52 | 234 | 682.5 | 235 | -40.0562 | 46.9649
2005-10-27 | 17:59 | 35 | 12.4 | -47.4 | 52 | 235 | 682.6 | 234 | -40.0875 | 46.7561
2005-10-27 | 18:59 | 33 | 11.9 | -47.8 | 52 | 237 | 682.5 | 237 | -40.3937 | 47.2661
2005-10-27 | 19:59 | 35 | 14.6 | -48 | 52 | 178 | 682.4 | 219 | -41.1562 | 43.4705
2005-10-27 | 20:59 | 40 | 11.1 | -49 | 51 | 209 | 682.4 | 196 | -42.875 | 38.4901
2005-10-27 | 21:59 | 42 | 14 | -48.7 | 51 | 208 | 682.2 | 208 | -42.2 | 41.0196
2005-10-27 | 22:59 | 36 | 13.7 | -47.1 | 53 | 264 | 682.1 | 242 | -39.5375 | 48.5185
2005-10-27 | 23:59 | 32 | 10.9 | -47.5 | 52 | 201 | 682.1 | 228 | -40.375 | 45.4764
2005-10-28 | 0:59 | 35 | 10.7 | -48 | 52 | 227 | 682 | 172 | -42.625 | 33.83
2005-10-28 | 1:59 | 34 | 11.7 | -47.1 | 53 | 275 | 681.9 | 256 | -39.1 | 51.4634
2005-10-28 | 2:59 | 51 | 6.2 | -48.9 | 51 | 279 | 682 | 278 | -40.2125 | 55.505
2005-10-28 | 3:59 | 47 | 10.1 | -49.4 | 51 | 262 | 681.9 | 268 | -41.025 | 53.2401
2005-10-28 | 4:59 | 41 | 11.2 | -49 | 51 | 246 | 681.9 | 234 | -41.6875 | 46.2948
2005-10-28 | 5:59 | 39 | 10.8 | -47.9 | 52 | 261 | 681.8 | 204 | -41.525 | 40.4004
2005-10-28 | 6:59 | 59 | 7 | -50.2 | 50 | 246 | 681.7 | 250 | -42.3875 | 49.2447
2005-10-28 | 7:59 | 48 | 6.8 | -51 | 49 | 269 | 681.9 | 242 | -43.4375 | 47.3558
2005-10-28 | 8:59 | 57 | 8 | -50.3 | 50 | 289 | 681.8 | 290 | -41.2375 | 57.5347
2005-10-28 | 9:59 | 72 | 7.4 | -50.5 | 50 | 240 | 681.8 | 254 | -42.5625 | 49.9778
2005-10-28 | 10:59 | 51 | 8.8 | -49.8 | 50 | 237 | 681.6 | 223 | -42.8312 | 43.8043
2005-10-28 | 11:59 | 61 | 9.1 | -50.2 | 50 | 266 | 681.5 | 254 | -42.2625 | 50.0717
2005-10-28 | 12:59 | 68 | 8.6 | -49.8 | 50 | 221 | 681.5 | 262 | -41.6125 | 51.8586
2005-10-28 | 13:59 | 68 | 9.5 | -50.1 | 50 | 235 | 681.4 | 227 | -43.0063 | 44.5411
2005-10-28 | 14:59 | 60 | 11.8 | -49.6 | 51 | 242 | 681.1 | 228 | -42.475 | 44.8865
2005-10-28 | 15:59 | 70 | 8.8 | -50.9 | 49 | 217 | 681.2 | 240 | -43.4 | 46.9755
2005-10-28 | 16:59 | 72 | 9.2 | -50.6 | 50 | 225 | 681.3 | 222 | -43.6625 | 43.3805
2005-10-28 | 17:59 | 68 | 8.2 | -50.3 | 50 | 246 | 681.1 | 227 | -43.2062 | 44.4852
2005-10-28 | 18:59 | 93 | 7.6 | -50.9 | 50 | 248 | 681.1 | 248 | -43.15 | 48.6177
2005-10-28 | 19:59 | 84 | 7.7 | -50.8 | 50 | 244 | 680.9 | 231 | -43.5812 | 45.1623
2005-10-28 | 20:59 | 86 | 7.5 | -50.3 | 51 | 220 | 680.9 | 230 | -43.1125 | 45.0996
2005-10-28 | 21:59 | 82 | 6.8 | -50.9 | 51 | 208 | 680.9 | 207 | -44.4312 | 40.2534
2005-10-28 | 22:59 | 86 | 8.5 | -50.8 | 51 | 226 | 680.7 | 214 | -44.1125 | 41.6986
2005-10-28 | 23:59 | 80 | 9.7 | -50.2 | 51 | 252 | 680.7 | 230 | -43.0125 | 45.128
2005-10-29 | 0:59 | 89 | 8.8 | -50.8 | 51 | 229 | 680.6 | 246 | -43.1125 | 48.237
2005-10-29 | 1:59 | 79 | 10.7 | -49.8 | 52 | 241 | 680.4 | 246 | -42.1125 | 48.5401
2005-10-29 | 2:59 | 109 | 5.9 | -49.7 | 52 | 289 | 680.3 | 274 | -41.1375 | 54.3941
2005-10-29 | 3:59 | 97 | 8.5 | -49.7 | 52 | 265 | 680 | 284 | -40.825 | 56.4886
2005-10-29 | 4:59 | 85 | 7.6 | -49.8 | 52 | 267 | 679.8 | 268 | -41.425 | 53.1081
2005-10-29 | 5:59 | 68 | 4.3 | -49.5 | 52 | 264 | 679.7 | 209 | -42.9688 | 41.0189
2005-10-29 | 6:59 | 111 | 6.1 | -49.6 | 52 | 238 | 679.6 | 246 | -41.9125 | 48.6007
2005-10-29 | 7:59 | 98 | 9.4 | -50 | 52 | 304 | 679.5 | 275 | -41.4062 | 54.5016
2005-10-29 | 8:59 | 80 | 7.7 | -49.5 | 52 | 288 | 679.3 | 282 | -40.6875 | 56.1386
2005-10-29 | 9:59 | 111 | 0 | -49.8 | 51 | 249 | 679.1 | 281 | -41.0187 | 55.8248
2005-10-29 | 10:59 | 95 | 5.4 | -48.5 | 53 | 276 | 679 | 274 | -39.9375 | 54.7992
2005-10-29 | 11:59 | 86 | 9.1 | -50 | 51 | 255 | 678.7 | 260 | -41.875 | 51.3786
2005-10-29 | 12:59 | 81 | 8.8 | -49.7 | 52 | 272 | 678.5 | 266 | -41.3875 | 52.724
2005-10-29 | 13:59 | 87 | 8 | -49.8 | 51 | 268 | 678.3 | 266 | -41.4875 | 52.6912
2005-10-29 | 14:59 | 74 | 8.8 | -49.8 | 51 | 258 | 678 | 260 | -41.675 | 51.4427
2005-10-29 | 15:59 | 95 | 8.8 | -50 | 51 | 216 | 677.8 | 249 | -42.2188 | 49.0994
2005-10-29 | 16:59 | 79 | 9.5 | -50 | 51 | 282 | 677.5 | 275 | -41.4062 | 54.5016
2005-10-29 | 17:59 | 75 | 9.1 | -49.1 | 52 | 263 | 677.5 | 277 | -40.4438 | 55.2264
2005-10-29 | 18:59 | 72 | 7.7 | -49.9 | 51 | 188 | 677.3 | 209 | -43.3687 | 40.9159
2005-10-29 | 19:59 | 86 | 7.8 | -50.1 | 51 | 197 | 677.3 | 189 | -44.1938 | 36.8084
2005-10-29 | 20:59 | 59 | 10.6 | -49 | 52 | 266 | 677 | 228 | -41.875 | 45.0551
2005-10-29 | 21:59 | 74 | 8.7 | -48.2 | 52 | 277 | 676.6 | 289 | -39.1688 | 58.0728
2005-10-29 | 22:59 | 97 | 7 | -49.6 | 51 | 207 | 676.4 | 227 | -42.5063 | 44.6809
2005-10-29 | 23:59 | 91 | 10.1 | -49.9 | 51 | 174 | 676.2 | 193 | -43.8687 | 37.6647
2005-10-30 | 0:59 | 81 | 10.9 | -49.8 | 51 | 244 | 676 | 206 | -43.3625 | 40.3301
2005-10-30 | 1:59 | 83 | 10.4 | -49.8 | 50 | 204 | 675.7 | 244 | -42.175 | 48.1267
2005-10-30 | 2:59 | 81 | 10.8 | -49.3 | 51 | 306 | 675.4 | 274 | -40.7375 | 54.5291
2005-10-30 | 3:59 | 73 | 7.9 | -49.4 | 50 | 288 | 675.1 | 305 | -39.8687 | 61.0249
2005-10-30 | 4:59 | 80 | 12.2 | -48.9 | 50 | 282 | 674.6 | 290 | -39.8375 | 58.0349
2005-10-30 | 5:59 | 84 | 7.4 | -49.4 | 50 | 298 | 674.6 | 216 | -42.65 | 42.4775
2005-10-30 | 6:59 | 80 | 7.6 | -49.5 | 50 | 297 | 674.3 | 295 | -40.2812 | 58.8742
2005-10-30 | 7:59 | 94 | 5.4 | -49.2 | 50 | 290 | 674.1 | 278 | -40.5125 | 55.4022
2005-10-30 | 8:59 | 85 | 8.5 | -49.5 | 50 | 290 | 673.7 | 291 | -40.4062 | 58.0311
2005-10-30 | 9:59 | 72 | 9.7 | -49.5 | 49 | 286 | 673.4 | 288 | -40.5 | 57.3996
2005-10-30 | 10:59 | 73 | 10.7 | -49.5 | 49 | 281 | 673.1 | 283 | -40.6562 | 56.3486
2005-10-30 | 11:59 | 79 | 8.6 | -49.7 | 49 | 274 | 672.9 | 277 | -41.0438 | 55.0216
2005-10-30 | 12:59 | 79 | 11.1 | -50 | 49 | 269 | 672.6 | 272 | -41.5 | 53.8756
2005-10-30 | 13:59 | 67 | 7.6 | -50.1 | 49 | 264 | 672.5 | 267 | -41.7563 | 52.8009
2005-10-30 | 14:59 | 76 | 10.1 | -50.4 | 49 | 260 | 672.2 | 262 | -42.2125 | 51.6649
2005-10-30 | 15:59 | 78 | 9 | -50.1 | 49 | 256 | 672 | 258 | -42.0375 | 50.9317
2005-10-30 | 16:59 | 76 | 11 | -50.6 | 49 | 254 | 671.8 | 255 | -42.6313 | 50.153
2005-10-30 | 17:59 | 70 | 12.5 | -50.2 | 49 | 255 | 671.7 | 255 | -42.2313 | 50.2786
2005-10-30 | 18:59 | 69 | 10.1 | -50.5 | 49 | 257 | 671.5 | 257 | -42.4688 | 50.5978
2005-10-30 | 19:59 | 70 | 12.7 | -50 | 50 | 257 | 671.3 | 256 | -42 | 50.5487
2005-10-30 | 20:59 | 67 | 12 | -50 | 50 | 260 | 671.3 | 254 | -42.0625 | 50.1343
2005-10-30 | 21:59 | 64 | 12.6 | -49.6 | 51 | 265 | 671.2 | 262 | -41.4125 | 51.9231
2005-10-30 | 22:59 | 70 | 10 | -49.9 | 50 | 270 | 671 | 266 | -41.5875 | 52.6585
2005-10-30 | 23:59 | 59 | 10 | -49.7 | 51 | 275 | 670.9 | 272 | -41.2 | 53.9761
2005-10-31 | 0:59 | 62 | 9.8 | -49.2 | 51 | 282 | 670.7 | 279 | -40.4813 | 55.6123
2005-10-31 | 1:59 | 57 | 10.9 | -48.6 | 51 | 287 | 670.5 | 284 | -39.725 | 56.8735
2005-10-31 | 2:59 | 58 | 10 | -49.1 | 51 | 293 | 670.5 | 290 | -40.0375 | 57.9634
2005-10-31 | 3:59 | 49 | 9.2 | -48.2 | 52 | 296 | 670.5 | 292 | -39.075 | 58.7094
2005-10-31 | 4:59 | 53 | 10.3 | -48.6 | 51 | 287 | 670.4 | 289 | -39.5688 | 57.9304
2005-10-31 | 5:59 | 56 | 10.8 | -48.4 | 51 | 293 | 670.5 | 218 | -41.5875 | 43.1562
2005-10-31 | 6:59 | 57 | 10.6 | -48.6 | 51 | 300 | 670.6 | 296 | -39.35 | 59.4134
2005-10-31 | 7:59 | 38 | 11.7 | -46.8 | 52 | 297 | 670.5 | 297 | -37.5187 | 60.2841
2005-10-31 | 8:59 | 57 | 8.6 | -46.7 | 52 | 294 | 670.6 | 293 | -37.5438 | 59.4632
2005-10-31 | 9:59 | 67 | 6.1 | -48.7 | 51 | 291 | 670.8 | 294 | -39.5125 | 58.9531
2005-10-31 | 10:59 | 67 | 8.8 | -49.5 | 50 | 286 | 670.8 | 289 | -40.4688 | 57.61
2005-10-31 | 11:59 | 75 | 7.5 | -49.1 | 50 | 281 | 670.9 | 283 | -40.2563 | 56.488
2005-10-31 | 12:59 | 63 | 8.2 | -49.8 | 50 | 275 | 671 | 277 | -41.1437 | 54.9875
2005-10-31 | 13:59 | 61 | 8.9 | -49.8 | 50 | 270 | 671.1 | 272 | -41.3 | 53.9426
2005-10-31 | 14:59 | 68 | 6.1 | -49.9 | 50 | 265 | 671.2 | 267 | -41.5562 | 52.8667
2005-10-31 | 15:59 | 61 | 8.5 | -50.2 | 50 | 262 | 671.2 | 264 | -41.95 | 52.1446
2005-10-31 | 16:59 | 58 | 9.3 | -49.9 | 51 | 260 | 671.4 | 261 | -41.7437 | 51.6184
2005-10-31 | 17:59 | 50 | 10.5 | -49.5 | 51 | 261 | 671.6 | 261 | -41.3438 | 51.747
2005-10-31 | 18:59 | 58 | 12 | -49.6 | 51 | 263 | 671.8 | 263 | -41.3813 | 52.1314
2005-10-31 | 19:59 | 62 | 10 | -49.8 | 51 | 263 | 672.1 | 262 | -41.6125 | 51.8586
2005-10-31 | 20:59 | 61 | 9.2 | -50.3 | 51 | 266 | 672.1 | 260 | -42.175 | 51.2825
2005-10-31 | 21:59 | 68 | 8.4 | -50.6 | 51 | 271 | 672.4 | 269 | -42.1938 | 53.0515
2005-10-31 | 22:59 | 79 | 5.9 | -50 | 51 | 267 | 672.6 | 272 | -41.5 | 53.8756
2005-10-31 | 23:58 | 57 | 11.5 | -49.6 | 52 | 283 | 672.5 | 278 | -40.9125 | 55.2652
2005-11-01 | 0:59 | 85 | 7 | -49.7 | 51 | 291 | 672.8 | 283 | -40.8563 | 56.2788
2005-11-01 | 1:59 | 76 | 8.2 | -49.9 | 51 | 295 | 672.9 | 289 | -40.8687 | 57.4676
2005-11-01 | 2:59 | 74 | 7.9 | -50.1 | 51 | 299 | 673.1 | 298 | -40.7875 | 59.287
2005-11-01 | 3:59 | 68 | 6.8 | -50.1 | 51 | 304 | 673.4 | 301 | -40.6938 | 59.9187
2005-11-01 | 4:59 | 71 | 7 | -50.3 | 51 | 288 | 673.5 | 305 | -40.7687 | 60.6867
2005-11-01 | 5:59 | 67 | 8.4 | -50.5 | 51 | 308 | 673.7 | 226 | -43.4375 | 44.2248
2005-11-01 | 6:59 | 57 | 10.3 | -50.1 | 51 | 308 | 674 | 307 | -40.5063 | 61.184
2005-11-01 | 7:59 | 66 | 6.5 | -49.6 | 52 | 307 | 674.4 | 308 | -39.975 | 61.5848
2005-11-01 | 8:59 | 59 | 8 | -49.8 | 51 | 304 | 674.6 | 303 | -40.3312 | 60.4521
2005-11-01 | 9:59 | 51 | 9.9 | -49.6 | 51 | 299 | 674.9 | 301 | -40.1938 | 60.1041
2005-11-01 | 10:59 | 47 | 10.2 | -49.4 | 52 | 294 | 675.1 | 297 | -40.1187 | 59.3328
2005-11-01 | 11:59 | 54 | 6.6 | -48.9 | 52 | 288 | 675.3 | 291 | -39.8062 | 58.2462
2005-11-01 | 12:59 | 41 | 11.9 | -49.8 | 51 | 283 | 675.4 | 285 | -40.8937 | 56.6634
2005-11-01 | 13:59 | 48 | 10 | -49.6 | 52 | 277 | 675.6 | 280 | -40.85 | 55.6844
2005-11-01 | 14:59 | 47 | 9.9 | -49.8 | 51 | 273 | 675.7 | 275 | -41.2062 | 54.5693
2005-11-01 | 15:59 | 42 | 12.2 | -49.2 | 52 | 270 | 675.7 | 272 | -40.7 | 54.1437
2005-11-01 | 16:59 | 51 | 12.1 | -49.4 | 52 | 265 | 676 | 266 | -41.0875 | 52.8223
2005-11-01 | 17:59 | 54 | 9.1 | -48.8 | 52 | 273 | 676.2 | 267 | -40.4562 | 53.2286
2005-11-01 | 18:59 | 83 | 6.8 | -50 | 51 | 273 | 676.8 | 273 | -41.4688 | 54.0842
2005-11-01 | 19:59 | 73 | 9.2 | -49.2 | 52 | 271 | 677 | 271 | -40.7313 | 53.9342
2005-11-01 | 20:59 | 65 | 10 | -49.9 | 51 | 274 | 677.1 | 267 | -41.5562 | 52.8667
2005-11-01 | 21:59 | 71 | 8.2 | -50.1 | 51 | 279 | 677.1 | 276 | -41.475 | 54.6764
2005-11-01 | 22:59 | 96 | 4.7 | -49.3 | 52 | 284 | 677.2 | 281 | -40.5187 | 55.9979
2005-11-01 | 23:59 | 77 | 9.5 | -49.7 | 51 | 290 | 677.3 | 287 | -40.7313 | 57.1185
2005-11-02 | 0:59 | 72 | 10.6 | -49.2 | 51 | 297 | 677.2 | 293 | -40.0438 | 58.5608
2005-11-02 | 1:59 | 70 | 11.7 | -48.9 | 51 | 303 | 677.2 | 300 | -39.525 | 60.1516
2005-11-02 | 2:59 | 82 | 9.2 | -49.5 | 51 | 308 | 677.2 | 306 | -39.9375 | 61.1991
2005-11-02 | 3:59 | 79 | 10.8 | -49 | 51 | 312 | 677.4 | 308 | -39.375 | 61.8125
2005-11-02 | 4:59 | 88 | 9.7 | -48.9 | 51 | 288 | 677.5 | 313 | -39.1187 | 62.9148
2005-11-02 | 5:59 | 91 | 10.2 | -48.9 | 51 | 315 | 677.7 | 230 | -41.7125 | 45.4963
2005-11-02 | 6:59 | 82 | 10.5 | -48.9 | 51 | 315 | 677.8 | 316 | -39.025 | 63.5543
2005-11-02 | 7:59 | 79 | 10.7 | -48.9 | 51 | 313 | 677.8 | 314 | -39.0875 | 63.1279
2005-11-02 | 8:59 | 73 | 11.8 | -48.4 | 51 | 310 | 677.8 | 309 | -38.7437 | 62.2535
2005-11-02 | 9:59 | 74 | 10.8 | -48.1 | 51 | 306 | 677.8 | 308 | -38.475 | 62.154
2005-11-02 | 10:59 | 73 | 10.1 | -48.9 | 51 | 300 | 677.7 | 303 | -39.4312 | 60.7881
2005-11-02 | 11:59 | 63 | 11.9 | -47.6 | 52 | 294 | 677.6 | 297 | -38.3188 | 59.9914
2005-11-02 | 12:59 | 69 | 9.8 | -47.9 | 52 | 288 | 677.6 | 291 | -38.8062 | 58.6047
2005-11-02 | 13:59 | 87 | 9.1 | -48.3 | 51 | 283 | 677.7 | 286 | -39.3625 | 57.4017
2005-11-02 | 14:59 | 86 | 8.7 | -48.1 | 51 | 279 | 677.6 | 281 | -39.3188 | 56.4134
2005-11-02 | 15:59 | 94 | 7.3 | -48.4 | 51 | 275 | 677.7 | 277 | -39.7437 | 55.4653
2005-11-02 | 16:59 | 73 | 8.4 | -48.1 | 52 | 273 | 677.6 | 274 | -39.5375 | 54.9342
2005-11-02 | 17:59 | 74 | 8.1 | -48.1 | 52 | 274 | 677.6 | 274 | -39.5375 | 54.9342
2005-11-02 | 18:59 | 90 | 8.7 | -48.1 | 51 | 277 | 677.7 | 276 | -39.475 | 55.3564
2005-11-02 | 19:59 | 74 | 10.6 | -47.8 | 52 | 278 | 677.7 | 277 | -39.1437 | 55.67
2005-11-02 | 20:59 | 83 | 9.9 | -48.3 | 51 | 274 | 677.5 | 272 | -39.8 | 54.4453
2005-11-02 | 21:59 | 72 | 11.2 | -48.2 | 51 | 283 | 677.3 | 275 | -39.6063 | 55.1114
2005-11-02 | 22:59 | 78 | 9.9 | -48.2 | 51 | 283 | 677.1 | 285 | -39.2938 | 57.2252
2005-11-02 | 23:59 | 79 | 10.3 | -47.8 | 51 | 289 | 677.1 | 289 | -38.7687 | 58.2153
2005-11-03 | 0:59 | 88 | 7.6 | -47.9 | 51 | 306 | 677.1 | 298 | -38.5875 | 60.0947
2005-11-03 | 1:59 | 87 | 8.5 | -47.8 | 51 | 312 | 676.8 | 310 | -38.1125 | 62.6961
2005-11-03 | 2:59 | 77 | 10.2 | -47.4 | 51 | 314 | 676.6 | 313 | -37.6187 | 63.4932
2005-11-03 | 3:59 | 83 | 7.9 | -47.7 | 51 | 315 | 676.3 | 309 | -38.0438 | 62.52
2005-11-03 | 4:59 | 71 | 9.9 | -47.6 | 51 | 305 | 676.1 | 308 | -37.975 | 62.3438
2005-11-03 | 5:59 | 91 | 8.2 | -47.7 | 51 | 310 | 676.1 | 231 | -40.4813 | 46.0446
2005-11-03 | 6:59 | 90 | 8.5 | -47.5 | 51 | 320 | 675.9 | 311 | -37.7812 | 63.0252
2005-11-03 | 7:59 | 99 | 7.1 | -47.2 | 51 | 320 | 675.6 | 319 | -37.2313 | 64.8626
2005-11-03 | 8:59 | 84 | 8.1 | -47.8 | 50 | 317 | 675.4 | 317 | -37.8937 | 64.1972
2005-11-03 | 9:59 | 95 | 6.8 | -47.3 | 51 | 313 | 675.1 | 315 | -37.4562 | 63.962
2005-11-03 | 10:59 | 82 | 8.6 | -47.2 | 51 | 307 | 674.7 | 310 | -37.5125 | 62.9252
2005-11-03 | 11:59 | 91 | 6.8 | -47.4 | 51 | 301 | 674.5 | 304 | -37.9 | 61.5622
2005-11-03 | 12:59 | 83 | 8.8 | -47.2 | 51 | 295 | 674.2 | 298 | -37.8875 | 60.3517
2005-11-03 | 13:59 | 95 | 8 | -46.9 | 51 | 290 | 674 | 293 | -37.7437 | 59.391
2005-11-03 | 14:59 | 100 | 5.6 | -47.1 | 51 | 286 | 673.8 | 288 | -38.1 | 58.2511
2005-11-03 | 15:59 | 88 | 6.2 | -47.8 | 50 | 282 | 673.5 | 284 | -38.925 | 57.1534
2005-11-03 | 16:59 | 82 | 7.6 | -47.7 | 51 | 280 | 673.3 | 281 | -38.9188 | 56.5518
2005-11-03 | 17:59 | 80 | 5.1 | -47.2 | 51 | 281 | 673.1 | 281 | -38.4188 | 56.7249
2005-11-03 | 18:59 | 98 | 5.2 | -45.6 | 52 | 284 | 673 | 284 | -36.725 | 57.9232
2005-11-03 | 19:59 | 94 | 6.8 | -46.9 | 50 | 283 | 672.7 | 283 | -38.0562 | 57.2551
2005-11-03 | 20:59 | 93 | 6.9 | -47.3 | 51 | 287 | 672.6 | 280 | -38.55 | 56.4778
2005-11-03 | 21:59 | 94 | 9 | -47.4 | 52 | 291 | 672.3 | 289 | -38.3687 | 58.3577
2005-11-03 | 22:59 | 86 | 8.7 | -47.1 | 53 | 297 | 672.1 | 294 | -37.9125 | 59.5326
2005-11-03 | 23:59 | 89 | 7.6 | -47.1 | 53 | 303 | 672 | 300 | -37.725 | 60.8168
2005-11-04 | 0:59 | 78 | 9.1 | -47 | 53 | 310 | 671.6 | 306 | -37.4375 | 62.1416
2005-11-04 | 1:59 | 104 | 6.9 | -46.1 | 54 | 316 | 671.6 | 313 | -36.3188 | 63.9945
2005-11-04 | 2:59 | 83 | 5.8 | -46.9 | 53 | 322 | 671.3 | 319 | -36.9312 | 64.9805
2005-11-04 | 3:59 | 89 | 5.8 | -46.6 | 54 | 325 | 671.1 | 322 | -36.5375 | 65.7478
2005-11-04 | 4:59 | 89 | 7.2 | -46.7 | 53 | 327 | 671 | 327 | -36.4813 | 66.7914
2005-11-04 | 5:59 | 77 | 8.3 | -47.1 | 52 | 329 | 670.9 | 243 | -39.5063 | 48.7284
2005-11-04 | 6:59 | 91 | 7.2 | -47.3 | 52 | 329 | 670.9 | 330 | -36.9875 | 67.1984
2005-11-04 | 7:59 | 96 | 7.1 | -46.8 | 51 | 327 | 671 | 328 | -36.55 | 66.9679
2005-11-04 | 8:59 | 101 | 6.3 | -47 | 51 | 324 | 670.8 | 323 | -36.9062 | 65.8053
2005-11-04 | 9:59 | 95 | 6.1 | -47 | 51 | 320 | 670.4 | 322 | -36.9375 | 65.5891
2005-11-04 | 10:59 | 78 | 7.1 | -47.4 | 51 | 313 | 670.2 | 317 | -37.4937 | 64.3534
2005-11-04 | 11:59 | 76 | 8.2 | -47.6 | 51 | 308 | 670.1 | 311 | -37.8813 | 62.9869
2005-11-04 | 12:59 | 74 | 7.4 | -47.9 | 50 | 302 | 670 | 305 | -38.3687 | 61.5886
2005-11-04 | 13:59 | 88 | 6.5 | -47.9 | 51 | 298 | 669.9 | 300 | -38.525 | 60.5212
2005-11-04 | 14:59 | 74 | 9.2 | -47.6 | 51 | 292 | 669.7 | 297 | -38.3188 | 59.9914
2005-11-04 | 15:59 | 70 | 8.8 | -48 | 51 | 298 | 669.4 | 295 | -38.7812 | 59.4193
2005-11-04 | 16:59 | 84 | 7.3 | -48.5 | 51 | 289 | 669.4 | 291 | -39.4062 | 58.3896
2005-11-04 | 17:59 | 81 | 7.3 | -48 | 51 | 289 | 669.5 | 286 | -39.0625 | 57.5074
2005-11-04 | 18:59 | 78 | 7.2 | -48.4 | 51 | 289 | 669.3 | 290 | -39.3375 | 58.2135
2005-11-04 | 19:59 | 75 | 7.5 | -48.5 | 51 | 286 | 669.1 | 290 | -39.4375 | 58.1778
2005-11-04 | 20:59 | 79 | 7.9 | -48.9 | 51 | 280 | 669 | 272 | -40.4 | 54.2442
2005-11-04 | 21:59 | 72 | 9.7 | -48.6 | 51 | 289 | 668.8 | 266 | -40.2875 | 53.0845
2005-11-04 | 22:59 | 73 | 8.3 | -48.3 | 51 | 278 | 668.5 | 282 | -39.4875 | 56.5555
2005-11-04 | 23:59 | 82 | 8.3 | -48.7 | 51 | 292 | 668.4 | 268 | -40.325 | 53.4713
2005-11-05 | 0:59 | 89 | 7.4 | -48.2 | 51 | 272 | 668.5 | 308 | -38.575 | 62.1161
2005-11-05 | 1:59 | 68 | 7.9 | -48.4 | 51 | 290 | 668.3 | 270 | -39.9625 | 53.9909
2005-11-05 | 2:59 | 79 | 6.6 | -48.3 | 51 | 305 | 668.4 | 296 | -39.05 | 59.5228
2005-11-05 | 3:59 | 61 | 7.2 | -47.9 | 51 | 342 | 668 | 317 | -37.9937 | 64.1582
2005-11-05 | 4:59 | 85 | 7.5 | -48.2 | 50 | 300 | 668.2 | 332 | -37.825 | 67.2631
2005-11-05 | 5:59 | 81 | 6.7 | -48.4 | 50 | 314 | 668.1 | 224 | -41.4 | 44.3957
2005-11-05 | 6:59 | 81 | 8.3 | -48 | 50 | 337 | 668.1 | 332 | -37.625 | 67.3449
2005-11-05 | 7:59 | 71 | 8.6 | -48 | 50 | 333 | 668.1 | 335 | -37.5312 | 67.9921
2005-11-05 | 8:59 | 82 | 9.3 | -48.1 | 50 | 330 | 668.1 | 329 | -37.8188 | 66.6578
2005-11-05 | 9:59 | 73 | 8.3 | -48.2 | 50 | 320 | 668.1 | 323 | -38.1063 | 65.3278
2005-11-05 | 10:59 | 82 | 7.8 | -48.3 | 50 | 318 | 668.1 | 312 | -38.55 | 62.9324
2005-11-05 | 11:59 | 72 | 8.6 | -48 | 50 | 306 | 668 | 314 | -38.1875 | 63.476
2005-11-05 | 12:59 | 78 | 8.9 | -48.2 | 50 | 310 | 667.9 | 310 | -38.5125 | 62.5433
2005-11-05 | 13:59 | 82 | 8 | -48.2 | 50 | 302 | 668 | 304 | -38.7 | 61.2626
2005-11-05 | 14:59 | 82 | 7.3 | -48.6 | 49 | 273 | 667.8 | 267 | -40.2563 | 53.2943
2005-11-05 | 15:59 | 84 | 6.2 | -48.1 | 50 | 279 | 667.8 | 282 | -39.2875 | 56.625
2005-11-05 | 16:59 | 83 | 7.6 | -48.4 | 50 | 240 | 667.7 | 286 | -39.4625 | 57.3665
2005-11-05 | 17:59 | 86 | 7.5 | -48.8 | 49 | 300 | 667.8 | 286 | -39.8625 | 57.2256
2005-11-05 | 18:59 | 92 | 6.9 | -48.8 | 49 | 297 | 667.8 | 299 | -39.4562 | 59.9764
2005-11-05 | 19:59 | 101 | 9.2 | -48.5 | 49 | 295 | 667.8 | 297 | -39.2188 | 59.6621
2005-11-05 | 20:59 | 97 | 9.6 | -48.8 | 49 | 298 | 667.8 | 292 | -39.675 | 58.4936
2005-11-05 | 21:59 | 80 | 7.8 | -48.9 | 49 | 305 | 667.6 | 301 | -39.4937 | 60.3637
2005-11-05 | 22:59 | 90 | 7.7 | -48.6 | 49 | 324 | 667.7 | 310 | -38.9125 | 62.3905
2005-11-05 | 23:59 | 88 | 8.1 | -48.8 | 48 | 330 | 667.7 | 305 | -39.2687 | 61.2504
2005-11-06 | 0:59 | 80 | 8 | -48.7 | 48 | 325 | 667.8 | 316 | -38.825 | 63.6322
2005-11-06 | 1:59 | 86 | 9.3 | -48.8 | 48 | 330 | 667.8 | 324 | -38.675 | 65.303
2005-11-06 | 2:59 | 76 | 9.7 | -49.1 | 48 | 334 | 667.7 | 331 | -38.7563 | 66.6807
2005-11-06 | 3:59 | 75 | 8.9 | -48.9 | 48 | 342 | 667.7 | 334 | -38.4625 | 67.4059
2005-11-06 | 4:59 | 76 | 4.5 | -49.5 | 47 | 341 | 667.8 | 333 | -39.0938 | 66.9452
2005-11-06 | 5:59 | 62 | 5.9 | -49 | 48 | 343 | 667.9 | 211 | -42.4062 | 41.5576
2005-11-06 | 6:59 | 64 | 10.6 | -48.8 | 48 | 343 | 667.9 | 343 | -38.0812 | 69.3834
2005-11-06 | 7:59 | 68 | 8.2 | -48.5 | 48 | 340 | 668 | 342 | -37.8125 | 69.2943
2005-11-06 | 8:59 | 61 | 8.4 | -48.6 | 48 | 337 | 668 | 337 | -38.0688 | 68.1749
2005-11-06 | 9:59 | 60 | 7.8 | -48.7 | 48 | 333 | 667.9 | 336 | -38.2 | 67.9182
2005-11-06 | 10:59 | 63 | 6.7 | -48.9 | 48 | 328 | 667.9 | 330 | -38.5875 | 66.5479
2005-11-06 | 11:59 | 59 | 6.7 | -49 | 48 | 322 | 667.8 | 324 | -38.875 | 65.2231
2005-11-06 | 12:59 | 57 | 7.8 | -48.4 | 48 | 316 | 667.9 | 319 | -38.4312 | 64.391
2005-11-06 | 13:59 | 57 | 8.2 | -48.7 | 48 | 311 | 667.9 | 313 | -38.9188 | 62.9919
2005-11-06 | 14:59 | 49 | 8 | -48.9 | 48 | 306 | 667.8 | 308 | -39.275 | 61.8505
2005-11-06 | 15:59 | 50 | 7.7 | -49.4 | 47 | 302 | 667.7 | 304 | -39.9 | 60.8131
2005-11-06 | 16:59 | 44 | 9 | -48.6 | 49 | 301 | 667.4 | 301 | -39.1938 | 60.4749
2005-11-06 | 17:59 | 46 | 10.3 | -48.3 | 49 | 301 | 667.5 | 301 | -38.8937 | 60.5862
2005-11-06 | 18:59 | 43 | 9.7 | -47.8 | 49 | 304 | 667.5 | 304 | -38.3 | 61.4124
2005-11-06 | 19:59 | 38 | 10.5 | -47.5 | 50 | 304 | 667.5 | 303 | -38.0312 | 61.3107
2005-11-06 | 20:59 | 29 | 13.6 | -47.1 | 51 | 307 | 667.4 | 299 | -37.7563 | 60.6026
2005-11-06 | 21:59 | 23 | 13.1 | -46.7 | 51 | 310 | 667.4 | 309 | -37.0438 | 62.9007
2005-11-06 | 22:59 | 27 | 12.7 | -46.4 | 52 | 317 | 667.3 | 313 | -36.6187 | 63.8788
2005-11-06 | 23:59 | 21 | 14.1 | -46.6 | 52 | 322 | 667.4 | 319 | -36.6313 | 65.0984
2005-11-07 | 0:59 | 22 | 12.3 | -46.8 | 52 | 337 | 667.6 | 327 | -36.5812 | 66.7511
2005-11-07 | 1:59 | 22 | 16 | -46.9 | 52 | 338 | 667.4 | 291 | -37.8062 | 58.9632
2005-11-07 | 2:59 | 16 | 17.9 | -46.7 | 52 | 314 | 667.4 | 344 | -35.95 | 70.4889
2005-11-07 | 3:59 | 13 | 15.2 | -46.6 | 52 | 332 | 667.4 | 329 | -36.3188 | 67.2658
2005-11-07 | 4:59 | 18 | 15.7 | -46.8 | 52 | 344 | 667.7 | 339 | -36.2062 | 69.3573
2005-11-07 | 5:59 | 14 | 17.8 | -46.6 | 52 | 286 | 667.8 | 245 | -38.9438 | 49.2992
2005-11-07 | 6:59 | 13 | 16.6 | -46.1 | 52 | 305 | 667.9 | 299 | -36.7563 | 60.971
2005-11-07 | 7:59 | 9 | 17.1 | -45.9 | 52 | 368 | 668.3 | 302 | -36.4625 | 61.692
2005-11-07 | 8:59 | 10 | 14.6 | -46.2 | 52 | 270 | 668.3 | 294 | -37.0125 | 59.8586
2005-11-07 | 9:59 | 17 | 16.2 | -45.9 | 52 | 334 | 668.4 | 335 | -35.4312 | 68.8588
2005-11-07 | 10:59 | 18 | 13.1 | -45.6 | 52 | 268 | 668.5 | 310 | -35.9125 | 63.5363
2005-11-07 | 11:59 | 11 | 14.3 | -45.5 | 52 | 259 | 668.9 | 287 | -36.5312 | 58.6035
2005-11-07 | 12:59 | 15 | 15.6 | -45.6 | 52 | 343 | 669.1 | 288 | -36.6 | 58.7833
2005-11-07 | 13:59 | 11 | 16.1 | -45.2 | 53 | 334 | 669.1 | 283 | -36.3563 | 57.8478
2005-11-07 | 14:59 | 10 | 17.7 | -45.4 | 53 | 273 | 669.2 | 309 | -35.7437 | 63.3956
2005-11-07 | 15:59 | 18 | 16 | -45.5 | 52 | 321 | 669.5 | 307 | -35.9062 | 62.9238
2005-11-07 | 16:59 | 24 | 10.5 | -45.8 | 52 | 290 | 669.8 | 308 | -36.175 | 63.0268
2005-11-07 | 17:59 | 21 | 11.8 | -46.1 | 52 | 256 | 670 | 279 | -37.3813 | 56.6778
2005-11-07 | 18:59 | 14 | 14 | -46.2 | 52 | 311 | 670.2 | 279 | -37.4813 | 56.6434
2005-11-07 | 19:59 | 12 | 14.9 | -45.8 | 52 | 287 | 670.3 | 281 | -37.0187 | 57.2096
2005-11-07 | 20:59 | 20 | 13 | -46.1 | 52 | 262 | 670.6 | 280 | -37.35 | 56.8917
2005-11-07 | 21:59 | 21 | 12.9 | -46.3 | 52 | 308 | 670.7 | 300 | -36.925 | 61.1125
2005-11-07 | 22:59 | 14 | 11.9 | -46.5 | 52 | 318 | 671 | 313 | -36.7188 | 63.8403
2005-11-07 | 23:59 | 25 | 11.5 | -46.5 | 52 | 336 | 671.1 | 333 | -36.0938 | 68.1759
2005-11-08 | 0:59 | 23 | 9.6 | -46.6 | 51 | 333 | 671.3 | 328 | -36.35 | 67.0487
2005-11-08 | 1:59 | 21 | 8.9 | -46.7 | 51 | 349 | 671.3 | 335 | -36.2313 | 68.5286
2005-11-08 | 2:59 | 23 | 8.4 | -46.9 | 51 | 347 | 671.4 | 346 | -36.0875 | 70.8401
2005-11-08 | 3:59 | 47 | 8.9 | -46.8 | 51 | 349 | 671.5 | 346 | -35.9875 | 70.8827
2005-11-08 | 4:59 | 30 | 10.5 | -46.7 | 51 | 350 | 671.6 | 350 | -35.7625 | 71.7992
2005-11-08 | 5:59 | 33 | 8.4 | -46.6 | 51 | 361 | 671.8 | 244 | -38.975 | 49.0886
2005-11-08 | 6:59 | 40 | 7.6 | -46.1 | 51 | 403 | 671.9 | 383 | -34.1313 | 79.3386
2005-11-08 | 7:59 | 46 | 7.3 | -46 | 51 | 386 | 672.1 | 403 | -33.4062 | 83.8415
2005-11-08 | 8:59 | 59 | 7.6 | -46.4 | 51 | 355 | 672.2 | 367 | -34.9312 | 75.6624
2005-11-08 | 9:59 | 58 | 6.9 | -46.7 | 51 | 344 | 672.2 | 349 | -35.7938 | 71.5806
2005-11-08 | 10:59 | 51 | 8 | -46.5 | 51 | 339 | 672.3 | 305 | -36.9688 | 62.1146
2005-11-08 | 11:59 | 47 | 7.3 | -46.8 | 51 | 345 | 672.4 | 333 | -36.3937 | 68.0528
2005-11-08 | 12:59 | 73 | 5.5 | -47.4 | 50 | 327 | 672.5 | 333 | -36.9937 | 67.8067
2005-11-08 | 13:59 | 69 | 7.6 | -47.3 | 50 | 321 | 672.5 | 324 | -37.175 | 65.9017
2005-11-08 | 14:59 | 74 | 6.6 | -47.8 | 50 | 316 | 672.5 | 319 | -37.8312 | 64.6268
2005-11-08 | 15:59 | 85 | 7.2 | -47.8 | 50 | 312 | 672.5 | 315 | -37.9562 | 63.7679
2005-11-08 | 16:59 | 91 | 5.4 | -47.6 | 50 | 311 | 672.5 | 312 | -37.85 | 63.2015
2005-11-08 | 17:59 | 84 | 6.3 | -47.7 | 50 | 312 | 672.6 | 312 | -37.95 | 63.163
2005-11-08 | 18:59 | 76 | 8 | -47.5 | 50 | 314 | 672.4 | 315 | -37.6562 | 63.8844
2005-11-08 | 19:59 | 78 | 9.2 | -47.5 | 50 | 314 | 672.3 | 314 | -37.6875 | 63.6695
2005-11-08 | 20:59 | 84 | 6.2 | -47.6 | 50 | 318 | 672.4 | 310 | -37.9125 | 62.7725
2005-11-08 | 21:59 | 80 | 6.4 | -47.7 | 50 | 323 | 672.2 | 320 | -37.7 | 64.8812
2005-11-08 | 22:59 | 82 | 7.5 | -47.5 | 50 | 329 | 672.2 | 326 | -37.3125 | 66.2533
2005-11-08 | 23:59 | 84 | 8.6 | -47.3 | 50 | 335 | 671.9 | 332 | -36.925 | 67.6312
2005-11-09 | 0:59 | 289 | 0 | -47.5 | 51 | 342 | 672 | 338 | -36.9375 | 68.8482
2005-11-09 | 1:59 | 78 | 6.5 | -47.2 | 51 | 348 | 671.7 | 345 | -36.4188 | 70.4946
2005-11-09 | 2:59 | 71 | 7.9 | -47.7 | 50 | 353 | 671.5 | 351 | -36.7313 | 71.5854
2005-11-09 | 3:59 | 77 | 7.9 | -47.6 | 50 | 357 | 671.4 | 353 | -36.5688 | 72.064
2005-11-09 | 4:59 | 71 | 5.5 | -47 | 50 | 360 | 671.4 | 359 | -35.7812 | 73.6372
2005-11-09 | 5:59 | 65 | 8.1 | -47.7 | 49 | 361 | 671.3 | 252 | -39.825 | 50.4342
2005-11-09 | 6:59 | 74 | 8.1 | -47.6 | 49 | 361 | 671.3 | 361 | -36.3188 | 73.8084
2005-11-09 | 7:59 | 67 | 7.4 | -47.7 | 48 | 359 | 671.4 | 360 | -36.45 | 73.5457
2005-11-09 | 8:59 | 60 | 6.2 | -47.3 | 49 | 356 | 671.4 | 355 | -36.2062 | 72.6308
2005-11-09 | 9:59 | 46 | 9.7 | -47 | 49 | 351 | 671.2 | 354 | -35.9375 | 72.5435
2005-11-09 | 10:59 | 51 | 8.5 | -46.6 | 48 | 344 | 671.2 | 348 | -35.725 | 71.405
2005-11-09 | 11:59 | 39 | 9.6 | -46.6 | 48 | 340 | 671 | 342 | -35.9125 | 70.0949
2005-11-09 | 12:59 | 40 | 11.3 | -46.4 | 48 | 333 | 671.1 | 336 | -35.9 | 68.8703
2005-11-09 | 13:59 | 31 | 7.9 | -46.5 | 48 | 328 | 671.1 | 331 | -36.1562 | 67.741
2005-11-09 | 14:59 | 36 | 9.6 | -46.3 | 49 | 323 | 671.1 | 325 | -36.1437 | 66.518
2005-11-09 | 15:59 | 26 | 10.8 | -46.3 | 49 | 319 | 671.4 | 321 | -36.2687 | 65.6499
2005-11-09 | 16:59 | 16 | 10 | -46.4 | 49 | 318 | 671.4 | 319 | -36.4312 | 65.177
2005-11-09 | 17:59 | 14 | 10.1 | -46.3 | 50 | 320 | 671.6 | 318 | -36.3625 | 64.9996
2005-11-09 | 18:59 | 12 | 15.9 | -46.3 | 50 | 316 | 671.7 | 312 | -36.55 | 63.7012
2005-11-09 | 19:59 | 9 | 17.8 | -46.5 | 51 | 175 | 671.8 | 234 | -39.1875 | 47.0155
2005-11-09 | 20:59 | 9 | 13.6 | -45.7 | 52 | 223 | 672.2 | 196 | -39.575 | 39.2869
2005-11-09 | 21:59 | 7 | 16.5 | -45.1 | 53 | 233 | 672.3 | 233 | -37.8188 | 47.2075
2005-11-09 | 22:59 | 11 | 15.4 | -44.5 | 54 | 208 | 672.4 | 230 | -37.3125 | 46.7431
2005-11-09 | 23:59 | 5 | 13.9 | -43.8 | 55 | 221 | 672.7 | 225 | -36.7687 | 45.8777
2005-11-10 | 0:59 | 1 | 17.4 | -43.3 | 55 | 231 | 672.8 | 229 | -36.1437 | 46.8696
2005-11-10 | 1:59 | 357 | 15.7 | -42.8 | 56 | 234 | 673 | 228 | -35.675 | 46.7966
2005-11-10 | 2:59 | 4 | 15.3 | -42.5 | 57 | 227 | 673.3 | 221 | -35.5938 | 45.382
2005-11-10 | 3:59 | 7 | 15 | -41.8 | 57 | 232 | 673.4 | 234 | -34.4875 | 48.3705
2005-11-10 | 4:59 | 9 | 15.7 | -41.4 | 58 | 266 | 673.7 | 240 | -33.9 | 49.7844
2005-11-10 | 5:59 | 0 | 15.2 | -41.1 | 58 | 213 | 674.1 | 270 | -32.6625 | 56.4191
2005-11-10 | 6:59 | 352 | 12.4 | -40.4 | 59 | 223 | 674.6 | 233 | -33.1187 | 48.5567
2005-11-10 | 7:59 | 3 | 15.4 | -39.8 | 59 | 223 | 674.8 | 250 | -31.9875 | 52.4479
2005-11-10 | 8:59 | 5 | 16 | -39.7 | 60 | 223 | 675 | 212 | -33.075 | 44.1917
2005-11-10 | 9:59 | 0 | 17.4 | -39.3 | 60 | 231 | 675.3 | 242 | -31.7375 | 50.8441
2005-11-10 | 10:59 | 0 | 15.2 | -39 | 60 | 220 | 675.7 | 234 | -31.6875 | 49.1777
2005-11-10 | 11:59 | 1 | 14.4 | -38.9 | 60 | 220 | 675.9 | 217 | -32.1187 | 45.4896
2005-11-10 | 12:59 | 348 | 13.4 | -38.7 | 60 | 232 | 676.2 | 225 | -31.6687 | 47.2914
2005-11-10 | 13:59 | 350 | 16.7 | -38.5 | 61 | 222 | 676.5 | 227 | -31.4062 | 47.7852
2005-11-10 | 14:59 | 346 | 12.5 | -38.4 | 61 | 255 | 677.1 | 231 | -31.1812 | 48.6913
2005-11-10 | 15:59 | 349 | 13.1 | -38.2 | 60 | 294 | 677.5 | 290 | -29.1375 | 61.8578
2005-11-10 | 16:59 | 351 | 9.4 | -38.3 | 60 | 246 | 678.1 | 300 | -28.925 | 64.0693
2005-11-10 | 17:59 | 0 | 10.6 | -38.6 | 60 | 229 | 678.5 | 220 | -31.725 | 46.2253
2005-11-10 | 18:59 | 0 | 11.9 | -38.8 | 59 | 207 | 679.1 | 313 | -29.0188 | 66.8095
2005-11-10 | 19:59 | 14 | 10.8 | -40.9 | 59 | 148 | 679.6 | 196 | -34.775 | 40.446
2005-11-10 | 20:59 | 8 | 13.7 | -40.4 | 60 | 245 | 679.9 | 201 | -34.1187 | 41.6403
2005-11-10 | 21:59 | 6 | 16.7 | -40 | 60 | 234 | 680 | 228 | -32.875 | 47.5831
2005-11-10 | 22:59 | 1 | 15 | -39.6 | 60 | 194 | 680.7 | 227 | -32.5063 | 47.4776
2005-11-10 | 23:59 | 0 | 14.2 | -39.2 | 60 | 241 | 680.9 | 215 | -32.4813 | 44.9744
2005-11-11 | 0:59 | 0 | 13.8 | -39 | 60 | 224 | 681.3 | 224 | -32 | 46.9898
2005-11-11 | 1:59 | 6 | 15.7 | -38.9 | 60 | 217 | 681.3 | 221 | -31.9937 | 46.3622
2005-11-11 | 2:59 | 5 | 14.6 | -38.6 | 61 | 212 | 681.4 | 215 | -31.8813 | 45.1333
2005-11-11 | 3:59 | 6 | 17.4 | -38.5 | 61 | 219 | 681.7 | 214 | -31.8125 | 44.9415
2005-11-11 | 4:59 | 12 | 17 | -38.2 | 61 | 213 | 681.9 | 215 | -31.4812 | 45.2392
2005-11-11 | 5:59 | 10 | 15.4 | -38.1 | 61 | 214 | 682.4 | 216 | -31.35 | 45.4846
2005-11-11 | 6:59 | 10 | 16 | -37.9 | 61 | 218 | 682.7 | 229 | -30.7437 | 48.3931
2005-11-11 | 7:59 | 17 | 16.3 | -37.8 | 61 | 207 | 683 | 222 | -30.8625 | 46.8814
2005-11-11 | 8:59 | 12 | 15.5 | -37.6 | 61 | 281 | 683.3 | 230 | -30.4125 | 48.6983
2005-11-11 | 9:59 | 15 | 16.3 | -37.4 | 61 | 239 | 683.2 | 268 | -29.025 | 57.2022
2005-11-11 | 10:59 | 13 | 12.4 | -36.9 | 62 | 299 | 683.2 | 266 | -28.5875 | 56.9187
2005-11-11 | 11:59 | 23 | 12.9 | -37.1 | 61 | 292 | 683.3 | 286 | -28.1625 | 61.3481
2005-11-11 | 12:59 | 31 | 11.7 | -37 | 58 | 307 | 683.3 | 283 | -28.1562 | 60.7068
2005-11-11 | 13:59 | 36 | 11.7 | -36.3 | 57 | 241 | 683.4 | 278 | -27.6125 | 59.8204
2005-11-11 | 14:59 | 39 | 11 | -35.7 | 56 | 291 | 683.5 | 247 | -27.9812 | 53.0376
2005-11-11 | 15:59 | 55 | 10.1 | -35.6 | 54 | 268 | 683.5 | 288 | -26.6 | 62.3315
2005-11-11 | 16:59 | 76 | 8.1 | -37.1 | 55 | 304 | 683.5 | 285 | -28.1938 | 61.1226
2005-11-11 | 17:59 | 83 | 11 | -38.2 | 54 | 317 | 683.4 | 318 | -28.2625 | 68.173
2005-11-11 | 18:59 | 81 | 10 | -38.8 | 52 | 325 | 683.5 | 326 | -28.6125 | 69.7475
2005-11-11 | 19:59 | 65 | 11.2 | -38.9 | 53 | 329 | 683.5 | 328 | -28.65 | 70.1602
2005-11-11 | 20:59 | 70 | 13.1 | -39.5 | 54 | 333 | 683.3 | 325 | -29.3438 | 69.2408
2005-11-11 | 21:59 | 59 | 13.7 | -39.1 | 55 | 337 | 683.4 | 335 | -28.6313 | 71.6653
2005-11-11 | 22:59 | 68 | 9.5 | -39.3 | 55 | 343 | 683.4 | 340 | -28.675 | 72.7166
2005-11-11 | 23:59 | 63 | 13.8 | -38.9 | 55 | 350 | 683.4 | 346 | -28.0875 | 74.2503
2005-11-12 | 0:59 | 76 | 9.9 | -38.8 | 55 | 356 | 683.3 | 353 | -27.7688 | 75.8911
2005-11-12 | 1:59 | M | M | M | M | M | M | 358 | 0 | 0 | - BAD DATA POINT
2005-11-12 | 5:59 | 72 | 12.9 | -35.8 | 59 | 374 | 682.7 | 303 | -26.3313 | 65.6782
2005-11-12 | 6:59 | 75 | 13.5 | -35.6 | 59 | 374 | 682.6 | 374 | -23.9125 | 82.1827
2005-11-12 | 7:59 | 76 | 14.1 | -35.4 | 59 | 372 | 682.5 | 373 | -23.7437 | 82.0405
2005-11-12 | 8:59 | 78 | 11.9 | -35.3 | 59 | 368 | 682.5 | 367 | -23.8313 | 80.6812
2005-11-12 | 9:59 | 70 | 15.2 | -34.2 | 60 | 363 | 682.3 | 364 | -22.825 | 80.473
2005-11-12 | 10:59 | 69 | 17.3 | -34.3 | 60 | 357 | 682.3 | 360 | -23.05 | 79.4889
2005-11-12 | 11:59 | 64 | 18.7 | -34.1 | 61 | 351 | 682.3 | 353 | -23.0688 | 77.9351
2005-11-12 | 12:59 | 59 | 16.3 | -33.6 | 62 | 345 | 682.4 | 348 | -22.725 | 76.9786
2005-11-12 | 13:59 | 69 | 18.7 | -33.5 | 62 | 340 | 682.2 | 343 | -22.7812 | 75.8488
2005-11-12 | 14:59 | 65 | 13.8 | -33.2 | 62 | 335 | 682.3 | 338 | -22.6375 | 74.803
2005-11-12 | 15:59 | 67 | 16.4 | -33.5 | 62 | 331 | 682.4 | 333 | -23.0938 | 73.5093
2005-11-12 | 16:59 | 67 | 15.2 | -33.6 | 62 | 330 | 682.6 | 330 | -23.2875 | 72.7682
2005-11-12 | 17:59 | 61 | 16.1 | -33.1 | 62 | 331 | 682.6 | 330 | -22.7875 | 72.9715
2005-11-12 | 18:59 | 58 | 18.2 | -32.7 | 63 | 333 | 682.5 | 333 | -22.2937 | 73.8375
2005-11-12 | 19:59 | 59 | 16.1 | -32.9 | 62 | 333 | 682.6 | 332 | -22.525 | 73.5211
2005-11-12 | 20:59 | 72 | 15.5 | -33.4 | 62 | 335 | 682.9 | 328 | -23.15 | 72.3828
2005-11-12 | 21:59 | 53 | 16.4 | -33.3 | 62 | 342 | 683.1 | 338 | -22.7375 | 74.7613
2005-11-12 | 22:59 | 66 | 15.5 | -34.1 | 61 | 290 | 683.3 | 313 | -24.3188 | 68.6219
2005-11-12 | 23:59 | 66 | 16.6 | -33.6 | 62 | 336 | 683.3 | 348 | -22.725 | 76.9786
2005-11-13 | 0:59 | 65 | 15.5 | -33.4 | 62 | 359 | 683.5 | 348 | -22.525 | 77.0643
2005-11-13 | 1:59 | 57 | 15.3 | -33.2 | 62 | 364 | 683.5 | 361 | -21.9187 | 80.2128
2005-11-13 | 2:59 | 58 | 17.1 | -33.3 | 63 | 370 | 683.7 | 366 | -21.8625 | 81.3491
2005-11-13 | 3:59 | 52 | 18.1 | -33.2 | 63 | 373 | 683.8 | 369 | -21.6687 | 82.104
2005-11-13 | 4:59 | 57 | 16.8 | -33.3 | 62 | 376 | 684 | 375 | -21.5813 | 83.4795
2005-11-13 | 5:59 | 49 | 18.4 | -33.1 | 62 | 377 | 684.5 | 260 | -24.975 | 56.792
2005-11-13 | 6:59 | 49 | 19.9 | -32.8 | 63 | 376 | 684.6 | 377 | -21.0188 | 84.1859
2005-11-13 | 7:59 | 50 | 22.6 | -33 | 63 | 374 | 684.7 | 375 | -21.2812 | 83.6181
2005-11-13 | 8:59 | 47 | 20.8 | -32.8 | 64 | 369 | 684.7 | 369 | -21.2688 | 82.2859
2005-11-13 | 9:59 | 47 | 22.7 | -32.5 | 65 | 363 | 684.5 | 366 | -21.0625 | 81.7099
2005-11-13 | 10:59 | 42 | 22.1 | -32.5 | 65 | 351 | 684.8 | 359 | -21.2812 | 80.0504
2005-11-13 | 11:59 | 42 | 23.9 | -32.6 | 65 | 352 | 684.9 | 354 | -21.5375 | 78.8237
2005-11-13 | 12:59 | 48 | 23.7 | -32.5 | 65 | 346 | 684.7 | 349 | -21.5938 | 77.6862
2005-11-13 | 13:59 | 48 | 21.6 | -32.6 | 65 | 338 | 684.5 | 343 | -21.8813 | 76.2291
2005-11-13 | 14:59 | 36 | 26.2 | -32.2 | 65 | 333 | 684.3 | 337 | -21.6687 | 74.9839
2005-11-13 | 15:59 | 38 | 22.2 | -32.2 | 66 | 328 | 684.2 | 331 | -21.8562 | 73.5724
2005-11-13 | 16:59 | 33 | 23.7 | -32.2 | 66 | 320 | 684.5 | 325 | -22.0437 | 72.1637
2005-11-13 | 17:59 | 39 | 22.8 | -32.5 | 65 | 326 | 684.2 | 323 | -22.4062 | 71.5753
2005-11-13 | 18:59 | 35 | 20.6 | -32.7 | 65 | 317 | 684.4 | 323 | -22.6062 | 71.4958
2005-11-13 | 19:59 | 29 | 21.9 | -32.9 | 65 | 319 | 684.5 | 319 | -22.9312 | 70.4826
2005-11-13 | 20:59 | 29 | 22.4 | -33.3 | 66 | 319 | 684.5 | 316 | -23.425 | 69.6276
2005-11-13 | 21:59 | 25 | 21.8 | -33.5 | 65 | 323 | 684.6 | 321 | -23.4688 | 70.712
2005-11-13 | 22:59 | 24 | 25.8 | -33.7 | 65 | 326 | 684.4 | 330 | -23.3875 | 72.7276
2005-11-13 | 23:59 | 22 | 24.7 | -33.8 | 65 | 332 | 684.5 | 333 | -23.3938 | 73.3862
2005-11-14 | 0:59 | 21 | 23.7 | -33.9 | 65 | 348 | 684.8 | 330 | -23.5875 | 72.6463
2005-11-14 | 1:59 | 23 | 23.1 | -34 | 65 | 318 | 685 | 328 | -23.75 | 72.1403
2005-11-14 | 2:59 | 16 | 21.9 | -34 | 65 | 337 | 685.2 | 341 | -23.3438 | 75.1702
2005-11-14 | 3:59 | 17 | 22.3 | -34.4 | 65 | 347 | 685.1 | 342 | -23.7125 | 75.2353
2005-11-14 | 4:59 | 24 | 20.2 | -34.3 | 64 | 333 | 685.2 | 351 | -23.3313 | 77.38
2005-11-14 | 5:59 | 24 | 26.2 | -34.5 | 64 | 354 | 685.4 | 274 | -25.9375 | 59.5251
2005-11-14 | 6:59 | 21 | 23.6 | -34.1 | 64 | 358 | 685.5 | 354 | -23.0375 | 78.1695
2005-11-14 | 7:59 | 20 | 21.1 | -33.7 | 65 | 395 | 685.7 | 369 | -22.1687 | 81.8767
2005-11-14 | 8:59 | 27 | 21.3 | -33.8 | 64 | 365 | 685.8 | 371 | -22.2063 | 82.3033
2005-11-14 | 9:59 | 25 | 18.6 | -34 | 64 | 363 | 686.2 | 361 | -22.7188 | 79.857
2005-11-14 | 10:59 | 21 | 23.2 | -33.9 | 64 | 359 | 686 | 362 | -22.5875 | 80.1367
2005-11-14 | 11:59 | 21 | 21.2 | -33.8 | 64 | 351 | 686.2 | 353 | -22.7688 | 78.0656
2005-11-14 | 12:59 | 23 | 19 | -33.9 | 64 | 349 | 686.3 | 349 | -22.9937 | 77.0842
2005-11-14 | 13:59 | 22 | 21.6 | -33.9 | 64 | 342 | 686.2 | 345 | -23.1187 | 76.1476
2005-11-14 | 14:59 | 18 | 19.3 | -33.8 | 64 | 341 | 686.4 | 342 | -23.1125 | 75.4881
2005-11-14 | 15:59 | 28 | 15.6 | -33.9 | 64 | 329 | 686.7 | 338 | -23.3375 | 74.5115
2005-11-14 | 16:59 | 19 | 23.4 | -33.9 | 65 | 335 | 686.4 | 326 | -23.7125 | 71.7155
2005-11-14 | 17:59 | 21 | 20.4 | -33.9 | 64 | 336 | 686.7 | 335 | -23.4312 | 73.8115
2005-11-14 | 18:59 | 17 | 21.2 | -34.1 | 64 | 326 | 686.9 | 336 | -23.6 | 73.9619
2005-11-14 | 19:59 | 19 | 18.8 | -34.2 | 64 | 337 | 687.4 | 338 | -23.6375 | 74.3866
2005-11-14 | 20:59 | 11 | 17.4 | -34.8 | 64 | 310 | 687.7 | 301 | -25.3938 | 65.5924
2005-11-14 | 21:59 | 21 | 17.4 | -34.8 | 65 | 330 | 687.9 | 281 | -26.0188 | 61.0177
2005-11-14 | 22:59 | 12 | 16.7 | -35.1 | 64 | 286 | 688.3 | 329 | -24.8188 | 71.9271
2005-11-14 | 23:59 | 13 | 19.4 | -34.8 | 64 | 386 | 688.3 | 339 | -24.2063 | 74.3691
2005-11-15 | 0:59 | 9 | 19.3 | -35 | 64 | 377 | 688.7 | 358 | -23.8125 | 78.711
2005-11-15 | 1:59 | 8 | 15.8 | -35 | 64 | 301 | 689.1 | 359 | -23.7812 | 78.9446
2005-11-15 | 2:59 | 7 | 16.7 | -35.1 | 64 | 335 | 689.6 | 302 | -25.6625 | 65.7103
2005-11-15 | 3:59 | 8 | 18.3 | -35.2 | 64 | 305 | 689.8 | 342 | -24.5125 | 74.8982
2005-11-15 | 4:59 | 5 | 15 | -34.9 | 64 | 334 | 690.2 | 342 | -24.2125 | 75.0246
2005-11-15 | 5:59 | 12 | 18 | -34.7 | 64 | 460 | 690.4 | 292 | -25.575 | 63.5659
2005-11-15 | 6:59 | 0 | 15.2 | -34.6 | 64 | 268 | 691.2 | 317 | -24.6938 | 69.3524
2005-11-15 | 7:59 | 3 | 10.3 | -35 | 63 | 357 | 691.7 | 297 | -25.7188 | 64.6018
2005-11-15 | 8:59 | 5 | 14 | -35.4 | 63 | 384 | 691.9 | 360 | -24.15 | 79.001
2005-11-15 | 9:59 | 8 | 14.5 | -35.8 | 62 | 384 | 692.3 | 374 | -24.1125 | 82.0905
2005-11-15 | 10:59 | 13 | 11.9 | -35.9 | 63 | 302 | 692.7 | 326 | -25.7125 | 70.9122
2005-11-15 | 11:59 | 7 | 12.6 | -35.7 | 63 | 360 | 692.9 | 365 | -24.2937 | 80.0336
2005-11-15 | 12:59 | 11 | 13 | -35.8 | 63 | 332 | 693.3 | 344 | -25.05 | 75.1084
2005-11-15 | 13:59 | 21 | 13.9 | -35.7 | 63 | 353 | 693.3 | 344 | -24.95 | 75.1508
2005-11-15 | 14:59 | 18 | 14 | -35.5 | 63 | 357 | 693.7 | 352 | -24.5 | 77.0936
2005-11-15 | 15:59 | 14 | 11.4 | -35.8 | 63 | 338 | 693.8 | 325 | -25.6438 | 70.7222
2005-11-15 | 16:59 | 19 | 10.2 | -35.4 | 63 | 267 | 693.9 | 312 | -25.65 | 67.891
2005-11-15 | 17:59 | 10 | 12.9 | -33.5 | 66 | 294 | 694 | 253 | -25.5938 | 55.0701
2005-11-15 | 18:59 | 2 | 12.7 | -33.5 | 65 | 340 | 694 | 293 | -24.3438 | 64.2281
2005-11-15 | 19:59 | 11 | 12.2 | -32.4 | 67 | 260 | 694.1 | 267 | -24.0562 | 58.6232
2005-11-15 | 20:59 | 16 | 13.2 | -32.1 | 67 | 358 | 694.1 | 292 | -22.975 | 64.5013
2005-11-15 | 21:59 | 8 | 15.9 | -32.7 | 67 | 295 | 694.3 | 315 | -22.8562 | 69.6279
2005-11-15 | 22:59 | 5 | 17.9 | -32.8 | 66 | 258 | 694.2 | 294 | -23.6125 | 64.7122
2005-11-15 | 23:59 | 8 | 17.2 | -33.4 | 65 | 279 | 694.3 | 315 | -23.5562 | 69.3563
2005-11-16 | 0:59 | 11 | 16.8 | -33.8 | 65 | 397 | 694.3 | 295 | -24.5813 | 64.5802
2005-11-16 | 1:59 | 10 | 15.2 | -33.8 | 65 | 297 | 694.4 | 339 | -23.2063 | 74.7868
2005-11-16 | 2:59 | 9 | 15.6 | -33.9 | 65 | 287 | 694.2 | 276 | -25.275 | 60.1849
2005-11-16 | 3:59 | 4 | 15.3 | -33.8 | 65 | 332 | 694 | 276 | -25.175 | 60.2189
2005-11-16 | 4:59 | 5 | 14.7 | -34.1 | 65 | 250 | 694 | 277 | -25.4438 | 60.3454
2005-11-16 | 5:59 | 10 | 16.2 | -34.3 | 65 | 239 | 694 | 269 | -25.8938 | 58.4534
2005-11-16 | 6:59 | 10 | 15.5 | -33.5 | 66 | 271 | 694.1 | 257 | -25.4688 | 55.9804
2005-11-16 | 7:59 | 3 | 16.1 | -32.9 | 66 | 253 | 694.1 | 241 | -25.3687 | 52.5249
2005-11-16 | 8:59 | 9 | 13.8 | -32.3 | 67 | 299 | 694 | 260 | -24.175 | 57.0483
2005-11-16 | 9:59 | 2 | 14.2 | -32.3 | 66 | 202 | 694.1 | 277 | -23.6438 | 60.9596
2005-11-16 | 10:59 | 0 | 13.6 | -32.2 | 66 | 262 | 694.3 | 255 | -24.2312 | 55.9335
2005-11-16 | 11:59 | 357 | 10.8 | -32.6 | 65 | 359 | 694.4 | 329 | -22.3188 | 72.9404
2005-11-16 | 12:59 | 2 | 11.8 | -33.1 | 66 | 221 | 694.4 | 266 | -24.7875 | 58.164
2005-11-16 | 13:59 | 1 | 9.5 | -32.8 | 66 | 177 | 694.5 | 280 | -24.05 | 61.4797
2005-11-16 | 14:59 | 8 | 9.8 | -34.3 | 65 | 327 | 694.5 | 256 | -26.3 | 55.5004
2005-11-16 | 15:59 | 8 | 10.2 | -33.5 | 66 | 343 | 694.5 | 281 | -24.7188 | 61.4678
2005-11-16 | 16:59 | 4 | 10.4 | -33.6 | 65 | 351 | 694.6 | 344 | -22.85 | 76.0408
2005-11-16 | 17:59 | 3 | 10 | -33.6 | 64 | 347 | 694.6 | 354 | -22.5375 | 78.3876
2005-11-16 | 18:59 | 9 | 11.6 | -33.9 | 64 | 353 | 694.7 | 352 | -22.9 | 77.7875
2005-11-16 | 19:59 | 1 | 11.5 | -34.6 | 64 | 352 | 694.6 | 351 | -23.6313 | 77.2503
2005-11-16 | 20:59 | 10 | 11.1 | -34.9 | 64 | 350 | 694.7 | 345 | -24.1187 | 75.7226
2005-11-16 | 21:59 | 12 | 11.7 | -35.3 | 64 | 254 | 694.7 | 310 | -25.6125 | 67.4701
2005-11-16 | 22:59 | 3 | 9.4 | -35.2 | 64 | 242 | 694.8 | 258 | -27.1375 | 55.6678
2005-11-16 | 23:59 | 301 | 5.6 | -35.8 | 64 | 282 | 694.7 | 234 | -28.4875 | 50.1002
2005-11-17 | 0:59 | 3 | 8.9 | -35.3 | 64 | 310 | 694.8 | 299 | -25.9563 | 64.9493
2005-11-17 | 1:59 | 4 | 10 | -35.3 | 64 | 296 | 694.7 | 306 | -25.7375 | 66.5524
2005-11-17 | 2:59 | 7 | 8.3 | -35.1 | 63 | 375 | 694.7 | 326 | -24.9125 | 71.2335
2005-11-17 | 3:59 | 1 | 10.8 | -35.5 | 63 | 384 | 694.7 | 320 | -25.5 | 69.6909
2005-11-17 | 4:59 | 5 | 8.7 | -35.9 | 63 | 316 | 694.6 | 320 | -25.9 | 69.5332
2005-11-17 | 5:59 | 0 | 8 | -35.3 | 62 | 393 | 694.6 | 297 | -26.0188 | 64.492
2005-11-17 | 6:59 | 2 | 7.3 | -35.4 | 62 | 346 | 694.7 | 382 | -23.4625 | 84.1524
2005-11-17 | 7:59 | 8 | 6.9 | -35.8 | 62 | 360 | 694.6 | 340 | -25.175 | 74.1827
2005-11-17 | 8:59 | 0 | 7.2 | -35.5 | 62 | 369 | 694.6 | 370 | -23.9375 | 81.2923
2005-11-17 | 9:59 | 357 | 8.2 | -35.3 | 62 | 432 | 694.6 | 379 | -23.4563 | 83.4944
2005-11-17 | 10:59 | 0 | 7.8 | -35.1 | 62 | 406 | 694.7 | 364 | -23.725 | 80.0694
2005-11-17 | 11:59 | 340 | 8.2 | -34.6 | 62 | 369 | 694.5 | 372 | -22.975 | 82.1729
2005-11-17 | 12:59 | 332 | 6.7 | -34.4 | 63 | 229 | 694.5 | 275 | -25.8062 | 59.7868
2005-11-17 | 13:59 | 336 | 7.1 | -34.3 | 63 | 238 | 694.5 | 286 | -25.3625 | 62.3347
2005-11-17 | 14:59 | 333 | 6.6 | -34.2 | 63 | 395 | 694.5 | 298 | -24.8875 | 65.1245
2005-11-17 | 15:59 | 326 | 6.4 | -33.8 | 64 | 281 | 694.1 | 317 | -23.8938 | 69.6648
2005-11-17 | 16:59 | 325 | 6.4 | -33.8 | 64 | 281 | 694.2 | 287 | -24.8313 | 62.7405
2005-11-17 | 17:59 | 338 | 6.3 | -33.5 | 64 | 258 | 694.1 | 260 | -25.375 | 56.6639
2005-11-17 | 18:59 | 336 | 8.5 | -33.2 | 64 | 299 | 694 | 277 | -24.5437 | 60.6525
2005-11-17 | 19:59 | 324 | 9.4 | -32.7 | 64 | 266 | 694.1 | 277 | -24.0437 | 60.8231
2005-11-17 | 20:59 | 329 | 9.8 | -32.6 | 65 | 266 | 694 | 263 | -24.3813 | 57.6397
2005-11-17 | 21:59 | 317 | 7.5 | -31.9 | 66 | 268 | 693.9 | 268 | -23.525 | 59.0182
2005-11-17 | 22:59 | 334 | 8.2 | -31.6 | 66 | 282 | 693.8 | 285 | -22.6938 | 63.0538
2005-11-17 | 23:59 | 314 | 5.7 | -32.2 | 65 | 253 | 693.7 | 263 | -23.9812 | 57.7693
2005-11-18 | 0:59 | 318 | 5.6 | -32.4 | 65 | 282 | 693.5 | 258 | -24.3375 | 56.5578
2005-11-18 | 1:59 | 301 | 6.4 | -31.8 | 64 | 282 | 693.3 | 286 | -22.8625 | 63.2156
2005-11-18 | 2:59 | 313 | 7.1 | -32.4 | 64 | 207 | 693.1 | 264 | -24.15 | 57.9341
2005-11-18 | 3:59 | 288 | 5.5 | -32.2 | 63 | 312 | 693 | 243 | -24.6062 | 53.1891
2005-11-18 | 4:59 | 292 | 7.8 | -32 | 60 | 251 | 692.7 | 293 | -22.8438 | 64.7696
2005-11-18 | 5:59 | 301 | 6.6 | -32.7 | 60 | 393 | 692.6 | 277 | -24.0437 | 60.8231
2005-11-18 | 6:59 | 309 | 4.9 | -33.7 | 61 | 348 | 692.4 | 360 | -22.45 | 79.755
2005-11-18 | 7:59 | 335 | 6.5 | -33.5 | 62 | 328 | 692 | 329 | -23.2188 | 72.5756
2005-11-18 | 8:59 | 323 | 6.6 | -33.2 | 61 | 358 | 691.6 | 322 | -23.1375 | 71.0637
2005-11-18 | 9:59 | 302 | 7 | -32.6 | 61 | 345 | 691.2 | 349 | -21.6938 | 77.6432
2005-11-18 | 10:59 | 295 | 8.2 | -32.7 | 60 | 386 | 690.8 | 358 | -21.5125 | 79.7254
2005-11-18 | 11:59 | 298 | 9.6 | -32.3 | 61 | 212 | 690.4 | 394 | -19.9875 | 88.4827
2005-11-18 | 12:59 | 300 | 9.3 | -31.7 | 63 | 352 | 690.2 | 300 | -22.325 | 66.5087
2005-11-18 | 13:59 | 307 | 6 | -31.8 | 62 | 277 | 689.7 | 316 | -21.925 | 70.2115
2005-11-18 | 14:59 | 311 | 7.6 | -31.6 | 62 | 438 | 689.3 | 347 | -20.7563 | 77.599
2005-11-18 | 15:59 | 307 | 8.8 | -32.1 | 63 | 257 | 688.8 | 308 | -22.475 | 68.2253
2005-11-18 | 16:59 | 316 | 7.7 | -31.3 | 64 | 367 | 688.3 | 333 | -20.8938 | 74.4118
2005-11-18 | 17:59 | 319 | 8.1 | -31.4 | 65 | 308 | 687.8 | 307 | -21.8062 | 68.2568
2005-11-18 | 18:59 | 307 | 9.9 | -30.5 | 67 | 320 | 687.3 | 287 | -21.5312 | 63.9073
2005-11-18 | 19:59 | 319 | 8.2 | -30.7 | 66 | 286 | 686.9 | 313 | -20.9187 | 69.933
2005-11-18 | 20:59 | 302 | 9.7 | -30.8 | 68 | 263 | 686.3 | 246 | -23.1125 | 54.2984
2005-11-18 | 21:59 | 288 | 9.9 | -29.7 | 69 | 233 | 686 | 303 | -20.2312 | 67.9554
2005-11-18 | 22:59 | 272 | 11.9 | -29.1 | 69 | 275 | 685.3 | 250 | -21.2875 | 55.7435
2005-11-18 | 23:59 | 273 | 10.1 | -28.2 | 70 | 411 | 684.8 | 291 | -19.1062 | 65.6674
2005-11-19 | 0:59 | 271 | 9.7 | -29.1 | 69 | 369 | 684.3 | 298 | -19.7875 | 66.9969
2005-11-19 | 1:59 | 251 | 8.1 | -30 | 68 | 364 | 683.8 | 408 | -17.25 | 93.0028
2005-11-19 | 2:59 | 241 | 6.7 | -31.3 | 68 | 368 | 683.4 | 372 | -19.675 | 83.6853
2005-11-19 | 3:59 | 220 | 7.5 | -30.9 | 68 | 406 | 683 | 372 | -19.275 | 83.8686
2005-11-19 | 4:59 | 206 | 6.9 | -31.4 | 66 | 401 | 682.7 | 401 | -18.8687 | 90.6074
2005-11-19 | 5:59 | 212 | 5.4 | -31.7 | 64 | 404 | 682.3 | 280 | -22.95 | 61.8592
2005-11-19 | 6:59 | 208 | 5 | -32.1 | 63 | 410 | 682 | 391 | -19.8813 | 87.8602
2005-11-19 | 7:59 | 185 | 5.4 | -34.1 | 63 | 405 | 681.7 | 405 | -21.4438 | 90.2264
2005-11-19 | 8:59 | 183 | 5.3 | -34.3 | 64 | 397 | 681.4 | 397 | -21.8938 | 88.2241
2005-11-19 | 9:59 | 182 | 5.6 | -34.8 | 63 | 394 | 681.2 | 395 | -22.4563 | 87.5059
2005-11-19 | 10:59 | 182 | 4.9 | -34.9 | 63 | 390 | 681.1 | 392 | -22.65 | 86.7477
2005-11-19 | 11:59 | 181 | 6.3 | -35.3 | 63 | 383 | 680.9 | 385 | -23.2688 | 84.9052
2005-11-19 | 12:59 | 133 | 6.7 | -34.9 | 63 | 376 | 680.7 | 379 | -23.0562 | 83.6812
2005-11-19 | 13:59 | 131 | 6.3 | -34.9 | 62 | 370 | 680.5 | 373 | -23.2437 | 82.2703
2005-11-19 | 14:59 | 125 | 7.8 | -35 | 62 | 366 | 680.2 | 368 | -23.5 | 81.0513
2005-11-19 | 15:59 | 142 | 9.8 | -35.4 | 62 | 363 | 680.1 | 364 | -24.025 | 79.9348
2005-11-19 | 16:59 | 130 | 9 | -35.5 | 62 | 360 | 680.1 | 361 | -24.2188 | 79.1899
2005-11-19 | 17:59 | 144 | 10.4 | -35.8 | 61 | 362 | 680 | 361 | -24.5188 | 79.0564
2005-11-19 | 18:59 | 121 | 10.5 | -36.1 | 60 | 366 | 680.1 | 365 | -24.6938 | 79.8537
2005-11-19 | 19:59 | 126 | 11.4 | -36 | 60 | 364 | 680 | 364 | -24.625 | 79.6658
2005-11-19 | 20:59 | 121 | 11.1 | -36.4 | 61 | 367 | 680 | 359 | -25.1812 | 78.3254
2005-11-19 | 21:59 | 113 | 12.9 | -36 | 61 | 373 | 680.1 | 370 | -24.4375 | 81.0644
2005-11-19 | 22:59 | 115 | 13 | -35.4 | 62 | 377 | 680.1 | 375 | -23.6812 | 82.5093
2005-11-19 | 23:59 | 123 | 16.1 | -35.4 | 62 | 382 | 680.2 | 380 | -23.525 | 83.6825
2005-11-20 | 0:59 | 127 | 17.7 | -35 | 62 | 391 | 680.3 | 387 | -22.9062 | 85.5191
2005-11-20 | 1:59 | 123 | 12.9 | -35 | 62 | 397 | 680.2 | 395 | -22.6562 | 87.4086
2005-11-20 | 2:59 | 126 | 19 | -35 | 62 | 402 | 679.9 | 400 | -22.5 | 88.592
2005-11-20 | 3:59 | 122 | 18.8 | -35.1 | 62 | 406 | 679.9 | 402 | -22.5375 | 89.0164
2005-11-20 | 4:59 | 122 | 15.9 | -35.1 | 62 | 406 | 679.9 | 406 | -22.4125 | 89.9646
2005-11-20 | 5:59 | 122 | 19 | -35 | 62 | 407 | 679.8 | 290 | -25.9375 | 63.001
2005-11-20 | 6:59 | 126 | 20.1 | -35.1 | 62 | 409 | 679.9 | 410 | -22.2875 | 90.9141
2005-11-20 | 7:59 | 124 | 17.6 | -35.4 | 62 | 407 | 679.9 | 409 | -22.6187 | 90.5255
2005-11-20 | 8:59 | 125 | 16.6 | -35.5 | 62 | 406 | 679.8 | 404 | -22.875 | 89.2913
2005-11-20 | 9:59 | 122 | 17 | -35.5 | 61 | 402 | 679.9 | 404 | -22.875 | 89.2913
2005-11-20 | 10:59 | 124 | 13.1 | -35.6 | 61 | 396 | 679.8 | 399 | -23.1313 | 88.0602
2005-11-20 | 11:59 | 122 | 14.7 | -35.6 | 62 | 390 | 679.8 | 392 | -23.35 | 86.4097
2005-11-20 | 12:59 | 121 | 12 | -35.7 | 61 | 384 | 679.8 | 387 | -23.6062 | 85.1853
2005-11-20 | 13:59 | 125 | 14.4 | -36 | 61 | 378 | 679.6 | 381 | -24.0938 | 83.6358
2005-11-20 | 14:59 | 131 | 17 | -36.2 | 61 | 374 | 679.3 | 376 | -24.45 | 82.3732
2005-11-20 | 15:59 | 123 | 16.4 | -36.3 | 60 | 370 | 679.4 | 372 | -24.675 | 81.3937
2005-11-20 | 16:59 | 134 | 12.2 | -36.6 | 61 | 369 | 679.4 | 369 | -25.0688 | 80.5583
2005-11-20 | 17:59 | 123 | 15.6 | -36.7 | 60 | 370 | 679.4 | 369 | -25.1687 | 80.5129
2005-11-20 | 18:59 | 132 | 12 | -36.7 | 60 | 375 | 679.5 | 373 | -25.0437 | 81.4431
2005-11-20 | 19:59 | 125 | 15.8 | -36.7 | 59 | 373 | 679.6 | 372 | -25.075 | 81.2104
2005-11-20 | 20:59 | 124 | 12.3 | -37.1 | 59 | 376 | 679.7 | 366 | -25.6625 | 79.6357
2005-11-20 | 21:59 | 142 | 14.1 | -36.8 | 59 | 381 | 679.8 | 378 | -24.9875 | 82.561
2005-11-20 | 22:59 | 124 | 16 | -36.5 | 59 | 387 | 679.8 | 384 | -24.5 | 84.1021
2005-11-20 | 23:59 | 135 | 12.7 | -36.5 | 59 | 394 | 679.9 | 390 | -24.3125 | 85.5063
2005-11-21 | 0:59 | 135 | 13.9 | -36.3 | 59 | 400 | 680 | 397 | -23.8938 | 87.2459
2005-11-21 | 1:59 | 143 | 13.2 | -36.1 | 59 | 406 | 680.1 | 403 | -23.5063 | 88.7568
2005-11-21 | 2:59 | 130 | 13.1 | -36 | 59 | 411 | 680.1 | 409 | -23.2188 | 90.2232
2005-11-21 | 3:59 | 129 | 14.4 | -35.8 | 60 | 415 | 680 | 410 | -22.9875 | 90.5606
2005-11-21 | 4:59 | 134 | 11.4 | -36.1 | 60 | 417 | 680.4 | 416 | -23.1 | 91.8282
2005-11-21 | 5:59 | 135 | 11.1 | -35.9 | 59 | 418 | 680.6 | 292 | -26.775 | 63.1343
2005-11-21 | 6:59 | 141 | 11.3 | -36 | 59 | 418 | 680.6 | 419 | -22.9062 | 92.5904
2005-11-21 | 7:59 | 146 | 9.7 | -36 | 60 | 416 | 680.9 | 417 | -22.9688 | 92.1163
2005-11-21 | 8:59 | 150 | 9.3 | -36.4 | 61 | 412 | 680.9 | 411 | -23.5562 | 90.4934
2005-11-21 | 9:59 | 161 | 9.6 | -36.8 | 61 | 408 | 681.2 | 410 | -23.9875 | 90.0554
2005-11-21 | 10:59 | 151 | 8.8 | -37.1 | 61 | 402 | 681.2 | 405 | -24.4438 | 88.7295
2005-11-21 | 11:59 | 147 | 6.9 | -37.1 | 61 | 394 | 681.3 | 397 | -24.6938 | 86.8546
2005-11-21 | 12:59 | 157 | 6.7 | -37.2 | 60 | 388 | 681.5 | 391 | -24.9812 | 85.4034
2005-11-21 | 13:59 | 145 | 7 | -37.2 | 60 | 383 | 681.5 | 384 | -25.2 | 83.771
2005-11-21 | 14:59 | 140 | 6.7 | -36.9 | 60 | 382 | 681.5 | 381 | -24.9937 | 83.2133
2005-11-21 | 15:59 | 144 | 11.1 | -36.9 | 59 | 373 | 681.4 | 373 | -25.2437 | 81.3512
2005-11-21 | 16:59 | 145 | 9.1 | -37.1 | 59 | 372 | 681.7 | 373 | -25.4438 | 81.2593
2005-11-21 | 17:59 | 147 | 9.8 | -37.1 | 59 | 373 | 681.8 | 373 | -25.4438 | 81.2593
2005-11-21 | 18:59 | 149 | 11.2 | -37.1 | 59 | 378 | 682.2 | 376 | -25.35 | 81.9563
2005-11-21 | 19:59 | 151 | 10 | -37.2 | 59 | 375 | 682.5 | 375 | -25.4812 | 81.6777
2005-11-21 | 20:59 | 162 | 6.5 | -37.7 | 59 | 379 | 682.6 | 369 | -26.1687 | 80.0583
2005-11-21 | 21:59 | 148 | 11 | -37.5 | 59 | 384 | 682.6 | 381 | -25.5938 | 82.9317
2005-11-21 | 22:59 | 146 | 11.8 | -37.2 | 59 | 389 | 682.5 | 387 | -25.1062 | 84.4701
2005-11-21 | 23:59 | 148 | 10.5 | -37.2 | 59 | 396 | 682.7 | 392 | -24.95 | 85.6369
2005-11-22 | 0:59 | 141 | 10 | -37 | 59 | 402 | 682.8 | 399 | -24.5312 | 87.372
2005-11-22 | 1:59 | 131 | 5.2 | -36.9 | 59 | 408 | 682.9 | 405 | -24.2437 | 88.8293
2005-11-22 | 2:59 | 134 | 4.5 | -37 | 59 | 414 | 682.9 | 411 | -24.1562 | 90.1896
2005-11-22 | 3:59 | 114 | 5.7 | -37.2 | 60 | 417 | 683 | 413 | -24.2937 | 90.5586
2005-11-22 | 4:59 | 141 | 11.1 | -36.9 | 59 | 420 | 683.1 | 419 | -23.8062 | 92.1258
2005-11-22 | 5:59 | 135 | 9.6 | -36.5 | 60 | 421 | 683.1 | 292 | -27.375 | 62.9184
2005-11-22 | 6:59 | 136 | 10.1 | -36.4 | 60 | 421 | 683.1 | 421 | -23.2437 | 92.8573
2005-11-22 | 7:59 | 136 | 11.8 | -36.6 | 60 | 418 | 683.3 | 420 | -23.475 | 92.5171
2005-11-22 | 8:59 | 142 | 11.8 | -36.6 | 60 | 415 | 683.2 | 413 | -23.6938 | 90.8638
2005-11-22 | 9:59 | 144 | 12.2 | -36.6 | 60 | 411 | 683.3 | 413 | -23.6938 | 90.8638
2005-11-22 | 10:59 | 140 | 10.9 | -36.7 | 60 | 405 | 683.3 | 408 | -23.95 | 89.635
2005-11-22 | 11:59 | 143 | 10.3 | -36.8 | 60 | 399 | 683.5 | 402 | -24.2375 | 88.1744
2005-11-22 | 12:59 | 144 | 9.8 | -37 | 60 | 393 | 683.4 | 396 | -24.625 | 86.6694
2005-11-22 | 13:59 | 148 | 9.4 | -36.8 | 59 | 387 | 683.3 | 390 | -24.6125 | 85.3622
2005-11-22 | 14:59 | 123 | 10.2 | -37.1 | 58 | 383 | 683.3 | 385 | -25.0688 | 84.0514
2005-11-22 | 15:59 | 120 | 14.5 | -37.7 | 57 | 379 | 683.1 | 380 | -25.825 | 82.6058
2005-11-22 | 16:59 | 121 | 14.3 | -38 | 57 | 377 | 683.2 | 378 | -26.1875 | 82.0022
2005-11-22 | 17:59 | 122 | 17 | -38.1 | 56 | 378 | 683.3 | 377 | -26.3188 | 81.7243
2005-11-22 | 18:59 | 118 | 14.5 | -38.2 | 56 | 383 | 683.5 | 380 | -26.325 | 82.3717
2005-11-22 | 19:59 | 114 | 12.7 | -38.2 | 56 | 380 | 683.6 | 379 | -26.3562 | 82.1403
2005-11-22 | 20:59 | 113 | 12.9 | -38.5 | 56 | 384 | 683.7 | 374 | -26.8125 | 80.8465
2005-11-22 | 21:59 | 110 | 13.5 | -38.4 | 55 | 389 | 683.6 | 386 | -26.3375 | 83.6663
2005-11-22 | 22:59 | 101 | 13 | -38.1 | 55 | 394 | 683.7 | 392 | -25.85 | 85.2023
2005-11-22 | 23:59 | 109 | 10.9 | -38.1 | 55 | 401 | 683.8 | 397 | -25.6938 | 86.3655
2005-11-23 | 0:59 | 101 | 13.5 | -38 | 55 | 407 | 683.8 | 404 | -25.375 | 88.047
2005-11-23 | 1:59 | 103 | 13.5 | -37.9 | 55 | 413 | 683.6 | 410 | -25.0875 | 89.4998
2005-11-23 | 2:59 | 94 | 11.9 | -37.9 | 55 | 417 | 683.5 | 415 | -24.9312 | 90.6712
2005-11-23 | 3:59 | 92 | 12 | -37.7 | 56 | 421 | 683.4 | 417 | -24.6687 | 91.243
2005-11-23 | 4:59 | 90 | 11.7 | -37.6 | 56 | 424 | 683.5 | 423 | -24.3813 | 92.7057
2005-11-23 | 5:59 | 80 | 10.7 | -37.5 | 56 | 425 | 683.5 | 294 | -28.3125 | 63.0098
2005-11-23 | 6:59 | 83 | 12.5 | -37.3 | 56 | 425 | 683.5 | 425 | -24.0188 | 93.3338
2005-11-23 | 7:59 | 84 | 10.5 | -37.2 | 57 | 422 | 683.6 | 424 | -23.95 | 93.1501
2005-11-23 | 8:59 | 78 | 11.3 | -37.1 | 57 | 419 | 683.5 | 417 | -24.0688 | 91.5512
2005-11-23 | 9:59 | 79 | 12.3 | -37 | 57 | 414 | 683.4 | 417 | -23.9688 | 91.6026
2005-11-23 | 10:59 | 80 | 12.4 | -36.9 | 57 | 409 | 683.1 | 411 | -24.0562 | 90.2403
2005-11-23 | 11:59 | 84 | 10.9 | -36.8 | 57 | 403 | 683 | 406 | -24.1125 | 89.1143
2005-11-23 | 12:59 | 92 | 10.5 | -36.9 | 57 | 397 | 682.9 | 400 | -24.4 | 87.6557
2005-11-23 | 13:59 | 93 | 9.1 | -37.1 | 57 | 392 | 682.8 | 394 | -24.7875 | 86.1527
2005-11-23 | 14:59 | 90 | 9.5 | -37.2 | 58 | 387 | 682.5 | 389 | -25.0437 | 84.9366
2005-11-23 | 15:59 | 91 | 8.2 | -37.2 | 58 | 383 | 682.3 | 385 | -25.1687 | 84.004
2005-11-23 | 16:59 | 84 | 9.2 | -37.1 | 59 | 381 | 682.3 | 382 | -25.1625 | 83.3523
2005-11-23 | 17:59 | 87 | 9.5 | -36.9 | 59 | 382 | 682.2 | 382 | -24.9625 | 83.4464
2005-11-23 | 18:59 | 84 | 8.6 | -36.9 | 59 | 387 | 682.2 | 385 | -24.8687 | 84.1463
2005-11-23 | 19:59 | 85 | 10.2 | -36.7 | 59 | 384 | 682.3 | 383 | -24.7312 | 83.774
2005-11-23 | 20:59 | 90 | 9.4 | -36.9 | 59 | 387 | 682.3 | 378 | -25.0875 | 82.5145
2005-11-23 | 21:59 | 81 | 9.4 | -36.6 | 60 | 392 | 682.1 | 389 | -24.4438 | 85.2242
2005-11-23 | 22:59 | 83 | 9.2 | -36.4 | 60 | 397 | 682 | 395 | -24.0562 | 86.7273
2005-11-23 | 23:59 | 80 | 9 | -36.1 | 60 | 403 | 681.9 | 400 | -23.6 | 88.0499
2005-11-24 | 0:59 | 77 | 10.8 | -36 | 60 | 409 | 681.9 | 407 | -23.2812 | 89.7506
2005-11-24 | 1:59 | 84 | 8.3 | -35.9 | 60 | 416 | 681.9 | 413 | -22.9937 | 91.22
2005-11-24 | 2:59 | 86 | 9.6 | -35.8 | 60 | 421 | 681.8 | 419 | -22.7063 | 92.6937
2005-11-24 | 3:59 | 84 | 9.6 | -35.6 | 61 | 425 | 681.7 | 420 | -22.475 | 93.0345
2005-11-24 | 4:59 | 75 | 10.9 | -35.3 | 61 | 428 | 681.7 | 426 | -21.9875 | 94.6195
2005-11-24 | 5:59 | 82 | 10.3 | -35.2 | 61 | 428 | 681.7 | 299 | -25.8562 | 64.9862
2005-11-24 | 6:59 | 80 | 9.3 | -34.9 | 61 | 427 | 681.9 | 428 | -21.525 | 95.3076
2005-11-24 | 7:59 | 72 | 11.8 | -34.1 | 62 | 425 | 681.9 | 426 | -20.7875 | 95.2493
2005-11-24 | 8:59 | 79 | 12 | -34.2 | 62 | 405 | 681.9 | 420 | -21.075 | 93.759
2005-11-24 | 9:59 | 68 | 11.1 | -33.8 | 63 | 408 | 681.9 | 412 | -20.925 | 92.0492
2005-11-24 | 10:59 | 65 | 11.3 | -33.6 | 63 | 422 | 682 | 413 | -20.6938 | 92.3903
2005-11-24 | 11:59 | 65 | 9.4 | -33.2 | 63 | 418 | 682 | 407 | -20.4812 | 91.1546
2005-11-24 | 12:59 | 55 | 12.3 | -33.3 | 63 | 399 | 682 | 406 | -20.6125 | 90.865
2005-11-24 | 13:59 | 54 | 11.8 | -33.4 | 63 | 394 | 682.1 | 397 | -20.9937 | 88.6643
2005-11-24 | 14:59 | 53 | 11.8 | -33.3 | 63 | 387 | 682.3 | 392 | -21.05 | 87.5204
2005-11-24 | 15:59 | 53 | 9.6 | -33.7 | 63 | 385 | 682.4 | 387 | -21.6062 | 86.1389
2005-11-24 | 16:59 | 60 | 9.6 | -33.7 | 64 | 322 | 682.5 | 378 | -21.8875 | 84.0047
2005-11-24 | 17:59 | 62 | 8.3 | -33.5 | 65 | 430 | 682.7 | 334 | -23.0625 | 73.7429
2005-11-24 | 18:59 | 86 | 9.3 | -34 | 64 | 349 | 682.9 | 373 | -22.3438 | 82.6838
2005-11-24 | 19:59 | 67 | 10.1 | -32.9 | 65 | 391 | 682.8 | 364 | -21.525 | 81.056
2005-11-24 | 20:59 | 71 | 9.5 | -34 | 64 | 391 | 682.9 | 379 | -22.1562 | 84.1014
2005-11-24 | 21:59 | 74 | 10.5 | -33.8 | 64 | 417 | 682.9 | 393 | -21.5188 | 87.5167
2005-11-24 | 22:59 | 67 | 11 | -33 | 64 | 404 | 682.6 | 387 | -20.9062 | 86.4726
2005-11-24 | 23:59 | 68 | 11.7 | -33 | 62 | 407 | 682.7 | 404 | -20.375 | 90.5356
2005-11-25 | 0:59 | 66 | 11.7 | -33.2 | 61 | 414 | 682.6 | 411 | -20.3562 | 92.1138
2005-11-25 | 1:59 | 73 | 11.3 | -33.4 | 61 | 421 | 682.5 | 418 | -20.3375 | 93.6923
2005-11-25 | 2:59 | 70 | 11.2 | -33.7 | 61 | 427 | 682.5 | 424 | -20.45 | 94.9784
2005-11-25 | 3:59 | 69 | 12.7 | -33.9 | 61 | 431 | 682.4 | 426 | -20.5875 | 95.3542
2005-11-25 | 4:59 | 63 | 11.5 | -34.2 | 60 | 434 | 682.4 | 433 | -20.6687 | 96.8777
2005-11-25 | 5:59 | 63 | 11.1 | -34.3 | 60 | 435 | 682.7 | 305 | -24.7688 | 66.6989
2005-11-25 | 6:59 | 59 | 9.8 | -34.3 | 60 | 435 | 682.8 | 435 | -20.7063 | 97.3051
2005-11-25 | 7:59 | 58 | 9.8 | -34.5 | 61 | 432 | 682.9 | 433 | -20.9688 | 96.7177
2005-11-25 | 8:59 | 52 | 10.8 | -34.5 | 61 | 429 | 683 | 427 | -21.1562 | 95.2789
2005-11-25 | 9:59 | 50 | 9.8 | -34.6 | 61 | 424 | 682.9 | 426 | -21.2875 | 94.9868
2005-11-25 | 10:59 | 33 | 8.4 | -34.4 | 62 | 414 | 683.2 | 421 | -21.2437 | 93.8947
2005-11-25 | 11:59 | 43 | 7.8 | -34.4 | 62 | 403 | 683.5 | 415 | -21.4312 | 92.4606
2005-11-25 | 12:59 | 38 | 8.2 | -34.5 | 63 | 400 | 683.5 | 401 | -21.9688 | 89.0759
2005-11-25 | 13:59 | 30 | 8.4 | -34.7 | 63 | 440 | 683.7 | 388 | -22.575 | 85.8984
2005-11-25 | 14:59 | 17 | 7.8 | -34.3 | 64 | 420 | 683.7 | 389 | -22.1438 | 86.3265
2005-11-25 | 15:59 | 19 | 6.5 | -35.1 | 63 | 390 | 684 | 370 | -23.5375 | 81.4747
2005-11-25 | 16:59 | 5 | 7.1 | -35.4 | 64 | 390 | 684.2 | 390 | -23.2125 | 86.0349
2005-11-25 | 17:59 | 5 | 6.8 | -35.6 | 63 | 379 | 684.5 | 389 | -23.4438 | 85.7034
2005-11-25 | 18:59 | 11 | 4.4 | -36 | 64 | 396 | 684.8 | 394 | -23.6875 | 86.6867
2005-11-25 | 19:59 | 4 | 4.9 | -36.4 | 64 | 392 | 685 | 392 | -24.15 | 86.0233
2005-11-25 | 20:59 | 41 | 2 | -36.7 | 65 | 396 | 685.2 | 386 | -24.6375 | 84.4748
2005-11-25 | 21:59 | 19 | 2.6 | -37.9 | 64 | 401 | 685.4 | 398 | -25.4625 | 86.6964
2005-11-25 | 22:59 | 12 | 4.2 | -37.2 | 64 | 407 | 685.6 | 404 | -24.575 | 88.4451
2005-11-25 | 23:59 | 35 | 2.6 | -37.3 | 65 | 413 | 685.7 | 410 | -24.4875 | 89.8029
2005-11-26 | 0:59 | 12 | 4 | -37.1 | 65 | 419 | 685.9 | 416 | -24.1 | 91.3157
2005-11-26 | 1:59 | 26 | 2 | -37.8 | 64 | 425 | 686 | 422 | -24.6125 | 92.3663
2005-11-26 | 2:59 | 59 | 3.5 | -38.2 | 62 | 430 | 686.2 | 428 | -24.825 | 93.5675
2005-11-26 | 3:59 | 56 | 5.4 | -37.9 | 62 | 434 | 686.3 | 429 | -24.4937 | 93.9612
2005-11-26 | 4:59 | 71 | 6.1 | -37.8 | 61 | 437 | 686.5 | 435 | -24.2063 | 95.4294
2005-11-26 | 5:59 | 70 | 6.1 | -37.6 | 61 | 438 | 686.8 | 309 | -27.9438 | 66.3649
2005-11-26 | 6:59 | 75 | 6.1 | -37.7 | 60 | 438 | 687.1 | 438 | -24.0125 | 96.1921
2005-11-26 | 7:59 | 69 | 5.2 | -37.9 | 61 | 435 | 687.2 | 437 | -24.2437 | 95.848
2005-11-26 | 8:59 | 74 | 5.8 | -37.9 | 61 | 432 | 687.3 | 430 | -24.4625 | 94.1967
2005-11-26 | 9:59 | 71 | 6.2 | -37.7 | 61 | 427 | 687.4 | 430 | -24.2625 | 94.3027
2005-11-26 | 10:59 | 76 | 6.1 | -37.9 | 61 | 422 | 687.5 | 425 | -24.6187 | 93.0196
2005-11-26 | 11:59 | 76 | 6.8 | -37.9 | 61 | 416 | 687.7 | 418 | -24.8375 | 91.3749
2005-11-26 | 12:59 | 77 | 5.6 | -37.9 | 61 | 409 | 688 | 412 | -25.025 | 89.9681
2005-11-26 | 13:59 | 84 | 4.8 | -38.1 | 61 | 404 | 688.1 | 407 | -25.3813 | 88.6976
2005-11-26 | 14:59 | 77 | 6.2 | -38 | 62 | 399 | 688.4 | 402 | -25.4375 | 87.5801
2005-11-26 | 15:59 | 69 | 5.8 | -37.9 | 61 | 395 | 688.7 | 397 | -25.4937 | 86.4633
2005-11-26 | 16:59 | 70 | 5.5 | -38 | 61 | 394 | 688.9 | 394 | -25.6875 | 85.7159
2005-11-26 | 17:59 | 73 | 6.8 | -37.8 | 61 | 395 | 689.2 | 394 | -25.4875 | 85.813
2005-11-26 | 18:59 | 77 | 5.5 | -38.1 | 61 | 400 | 689.5 | 397 | -25.6938 | 86.3655
2005-11-26 | 19:59 | 72 | 5.1 | -38.1 | 61 | 397 | 689.8 | 396 | -25.725 | 86.1327
2005-11-26 | 20:59 | 70 | 5.6 | -38.2 | 61 | 400 | 689.9 | 390 | -26.0125 | 84.6895
2005-11-26 | 21:59 | 70 | 6 | -38.1 | 61 | 405 | 690.2 | 402 | -25.5375 | 87.5306
2005-11-26 | 22:59 | 65 | 4.3 | -38.1 | 61 | 410 | 690.3 | 408 | -25.35 | 88.9313
2005-11-26 | 23:59 | 69 | 6.6 | -37.7 | 61 | 417 | 690.5 | 414 | -24.7625 | 90.5387
2005-11-27 | 0:59 | 63 | 6.8 | -37.5 | 61 | 423 | 690.6 | 420 | -24.375 | 92.0514
2005-11-27 | 1:59 | 57 | 5.9 | -37.5 | 61 | 429 | 690.7 | 426 | -24.1875 | 93.4648
2005-11-27 | 2:59 | 60 | 6.7 | -37.4 | 61 | 435 | 690.7 | 432 | -23.9 | 94.9342
2005-11-27 | 3:59 | 66 | 7.2 | -37.4 | 61 | 438 | 690.7 | 434 | -23.8375 | 95.4072
2005-11-27 | 4:59 | 60 | 6.8 | -37.2 | 61 | 441 | 690.8 | 440 | -23.45 | 96.9362
2005-11-27 | 5:59 | 55 | 5.7 | -37.2 | 61 | 442 | 691 | 312 | -27.45 | 67.1991
2005-11-27 | 6:59 | 59 | 7.9 | -36.9 | 61 | 442 | 690.9 | 442 | -23.0875 | 97.5742
2005-11-27 | 7:59 | 57 | 6.3 | -36.8 | 61 | 439 | 691 | 441 | -23.0188 | 97.3908
2005-11-27 | 8:59 | 55 | 6.2 | -36.9 | 61 | 436 | 690.8 | 434 | -23.3375 | 95.6745
2005-11-27 | 9:59 | 47 | 6.9 | -36.6 | 61 | 432 | 690.8 | 434 | -23.0375 | 95.8349
2005-11-27 | 10:59 | 52 | 6.9 | -36.8 | 61 | 426 | 690.7 | 429 | -23.3938 | 94.5425
2005-11-27 | 11:59 | 50 | 8.5 | -36.3 | 62 | 420 | 690.8 | 422 | -23.1125 | 93.1461
2005-11-27 | 12:59 | 62 | 7 | -36.7 | 62 | 394 | 690.6 | 417 | -23.6687 | 91.7567
2005-11-27 | 13:59 | 57 | 6.6 | -36.6 | 62 | 405 | 690.5 | 409 | -23.8188 | 89.9208
2005-11-27 | 14:59 | 64 | 8.8 | -36.4 | 62 | 396 | 690.4 | 403 | -23.8062 | 88.6079
2005-11-27 | 15:59 | 63 | 7.8 | -36 | 62 | 394 | 690.1 | 395 | -23.6562 | 86.9219
2005-11-27 | 16:59 | 54 | 8.7 | -35.7 | 62 | 399 | 689.9 | 387 | -23.6062 | 85.1853
2005-11-27 | 17:59 | 45 | 7.2 | -35.8 | 62 | 354 | 689.9 | 390 | -23.6125 | 85.8427
2005-11-27 | 18:59 | 54 | 7.7 | -35 | 63 | 380 | 689.7 | 373 | -23.3438 | 82.2243
2005-11-27 | 19:59 | 56 | 7.7 | -35.6 | 64 | 394 | 689.4 | 365 | -24.1938 | 80.0786
2005-11-27 | 20:59 | 59 | 6.9 | -35.5 | 64 | 398 | 689.3 | 386 | -23.4375 | 85.0455
2005-11-27 | 21:59 | 69 | 6.4 | -36.4 | 63 | 401 | 689.1 | 388 | -24.275 | 85.0858
2005-11-27 | 22:59 | 63 | 6.4 | -36.2 | 63 | 420 | 688.9 | 407 | -23.4812 | 89.6503
2005-11-27 | 23:59 | 56 | 7.4 | -36 | 63 | 393 | 688.6 | 410 | -23.1875 | 90.4595
2005-11-28 | 0:59 | 60 | 7.3 | -36 | 62 | 431 | 688.3 | 426 | -22.6875 | 94.2521
2005-11-28 | 1:59 | 73 | 7.1 | -36.5 | 62 | 398 | 688 | 428 | -23.125 | 94.4639
2005-11-28 | 2:59 | 76 | 7.8 | -36.6 | 61 | 439 | 687.5 | 429 | -23.1938 | 94.6483
2005-11-28 | 3:59 | 72 | 7.8 | -36.5 | 61 | 442 | 687.2 | 437 | -22.8438 | 96.6017
2005-11-28 | 4:59 | 69 | 8.5 | -36.4 | 61 | 445 | 686.9 | 443 | -22.5562 | 98.0849
2005-11-28 | 5:59 | 70 | 7.8 | -36.4 | 60 | 446 | 686.5 | 314 | -26.5875 | 67.9635
2005-11-28 | 6:59 | 74 | 8 | -36.4 | 60 | 447 | 686.2 | 447 | -22.4312 | 99.0394
2005-11-28 | 7:59 | 75 | 7.9 | -36.5 | 59 | 444 | 685.8 | 446 | -22.5625 | 98.7457
2005-11-28 | 8:59 | 76 | 7.9 | -36.7 | 59 | 441 | 685.4 | 440 | -22.95 | 97.2073
2005-11-28 | 9:59 | 74 | 8.2 | -36.8 | 58 | 437 | 684.9 | 440 | -23.05 | 97.1531
2005-11-28 | 10:59 | 76 | 9.5 | -36.7 | 58 | 432 | 684.6 | 435 | -23.1062 | 96.0189
2005-11-28 | 11:59 | 75 | 10.2 | -36.7 | 58 | 426 | 684.1 | 428 | -23.325 | 94.3584
2005-11-28 | 12:59 | 75 | 8 | -37.2 | 59 | 420 | 683.9 | 423 | -23.9812 | 92.9141
2005-11-28 | 13:59 | 73 | 5.5 | -37.6 | 59 | 416 | 683.5 | 418 | -24.5375 | 91.5294
2005-11-28 | 14:59 | 71 | 7.9 | -37.2 | 60 | 416 | 682.8 | 415 | -24.2312 | 91.029
2005-11-28 | 15:59 | 58 | 7.1 | -36.4 | 61 | 417 | 682.6 | 423 | -23.1812 | 93.331
2005-11-28 | 16:59 | 64 | 8.9 | -37.1 | 61 | 405 | 682.2 | 388 | -24.975 | 84.7512
2005-11-28 | 17:59 | 54 | 8.6 | -37.1 | 61 | 400 | 682.1 | 403 | -24.5063 | 88.2603
2005-11-28 | 18:59 | 51 | 8.9 | -36.1 | 63 | 432 | 681.9 | 405 | -23.4438 | 89.2285
2005-11-28 | 19:59 | 47 | 10.4 | -36 | 63 | 394 | 681.7 | 414 | -23.0625 | 91.4058
2005-11-28 | 20:59 | 44 | 9.2 | -36.1 | 64 | 411 | 681.6 | 396 | -23.725 | 87.1084
2005-11-28 | 21:59 | 50 | 10.2 | -36.1 | 64 | 414 | 681.3 | 413 | -23.1938 | 91.1182
2005-11-28 | 22:59 | 42 | 8.8 | -36 | 64 | 419 | 681.1 | 416 | -23 | 91.8794
2005-11-28 | 23:59 | 47 | 9.4 | -36.2 | 63 | 426 | 681 | 423 | -22.9812 | 93.4352
2005-11-29 | 0:59 | 35 | 10.6 | -35.8 | 63 | 432 | 680.8 | 429 | -22.3938 | 95.0711
2005-11-29 | 1:59 | 47 | 8.1 | -36.4 | 63 | 439 | 680.6 | 436 | -22.775 | 96.4176
2005-11-29 | 2:59 | 46 | 10.7 | -36.1 | 63 | 444 | 680.5 | 442 | -22.2875 | 98.0099
2005-11-29 | 3:59 | 37 | 9.6 | -35.9 | 63 | 447 | 680.3 | 443 | -22.0562 | 98.3578
2005-11-29 | 4:59 | 47 | 8.7 | -35.9 | 62 | 450 | 680.1 | 449 | -21.8687 | 99.7937
2005-11-29 | 5:59 | 42 | 11.5 | -35.8 | 62 | 452 | 680 | 315 | -25.9563 | 68.4249
2005-11-29 | 6:59 | 44 | 11.1 | -35.7 | 61 | 452 | 680.1 | 452 | -21.575 | 100.6241
2005-11-29 | 7:59 | 39 | 9.9 | -35.6 | 61 | 448 | 680 | 450 | -21.5375 | 100.1996
2005-11-29 | 8:59 | 39 | 13.9 | -35.2 | 61 | 446 | 679.9 | 444 | -21.325 | 98.9799
2005-11-29 | 9:59 | 49 | 9 | -35.1 | 61 | 441 | 679.9 | 443 | -21.2563 | 98.7944
2005-11-29 | 10:59 | 42 | 10.5 | -34.8 | 62 | 435 | 679.7 | 438 | -21.1125 | 97.757
2005-11-29 | 11:59 | 44 | 11 | -34.4 | 62 | 429 | 679.9 | 432 | -20.9 | 96.5309
2005-11-29 | 12:59 | 40 | 11 | -34.1 | 62 | 423 | 679.9 | 426 | -20.7875 | 95.2493
2005-11-29 | 13:59 | 54 | 7.9 | -34.4 | 62 | 416 | 679.9 | 420 | -21.275 | 93.6555
2005-11-29 | 14:59 | 39 | 12.4 | -33.7 | 63 | 412 | 679.7 | 414 | -20.7625 | 92.5789
2005-11-29 | 15:59 | 36 | 12.9 | -33.6 | 63 | 406 | 679.6 | 409 | -20.8188 | 91.4325
2005-11-29 | 16:59 | 32 | 12.2 | -33.4 | 64 | 406 | 679.7 | 406 | -20.7125 | 90.815
2005-11-29 | 17:59 | 29 | 13 | -33.6 | 64 | 408 | 679.9 | 407 | -20.8813 | 90.954
2005-11-29 | 18:59 | 30 | 10 | -33.7 | 64 | 412 | 680.1 | 410 | -20.8875 | 91.6213
2005-11-29 | 19:59 | 32 | 12 | -33.7 | 64 | 407 | 680.3 | 409 | -20.9187 | 91.3821
2005-11-29 | 20:59 | 25 | 13.7 | -33.8 | 65 | 412 | 680.6 | 402 | -21.2375 | 89.6602
2005-11-29 | 21:59 | 19 | 12.6 | -33.8 | 65 | 419 | 680.9 | 415 | -20.8313 | 92.7674
2005-11-29 | 22:59 | 8 | 13.1 | -34 | 64 | 366 | 681.2 | 393 | -21.7188 | 87.4199
2005-11-29 | 23:59 | 11 | 12 | -33.5 | 65 | 316 | 681.5 | 397 | -21.0938 | 88.6154
2005-11-30 | 0:59 | 12 | 12.2 | -33.6 | 65 | 461 | 681.9 | 429 | -20.1938 | 96.2338
2005-11-30 | 1:59 | 9 | 10.7 | -33.7 | 65 | 442 | 682.2 | 431 | -20.2312 | 96.6626
2005-11-30 | 2:59 | 15 | 10 | -34 | 65 | 447 | 682.6 | 445 | -20.0938 | 99.8778
2005-11-30 | 3:59 | 10 | 11.7 | -34.1 | 65 | 451 | 682.9 | 446 | -20.1625 | 100.0645
2005-11-30 | 4:59 | 6 | 11.6 | -34 | 65 | 453 | 683.5 | 452 | -19.875 | 101.5707
2005-11-30 | 5:59 | 10 | 14.5 | -34.1 | 64 | 454 | 684 | 315 | -24.2563 | 69.0846
2005-11-30 | 6:59 | 10 | 11.6 | -34 | 64 | 455 | 684.6 | 455 | -19.7812 | 102.2974
2005-11-30 | 7:59 | 11 | 11.1 | -33.9 | 64 | 452 | 685.2 | 453 | -19.7437 | 101.8687
2005-11-30 | 8:59 | 16 | 10.7 | -34 | 64 | 448 | 685.8 | 447 | -20.0312 | 100.3611
2005-11-30 | 9:59 | 23 | 9.6 | -33.9 | 64 | 444 | 686.3 | 446 | -19.9625 | 100.1744
2005-11-30 | 10:59 | 21 | 11.5 | -33.8 | 64 | 439 | 686.8 | 441 | -20.0188 | 99.0208
2005-11-30 | 11:59 | 14 | 10.9 | -33.5 | 64 | 431 | 687 | 435 | -19.9062 | 97.7338
2005-11-30 | 12:59 | 16 | 12.8 | -33.5 | 64 | 424 | 687.5 | 428 | -20.125 | 96.0458
2005-11-30 | 13:59 | 15 | 10.6 | -33.4 | 64 | 419 | 687.9 | 422 | -20.2125 | 94.6538
2005-11-30 | 14:59 | 21 | 8 | -33.5 | 65 | 415 | 688.1 | 417 | -20.4688 | 93.4007
2005-11-30 | 15:59 | 21 | 8.7 | -33.4 | 66 | 411 | 688.4 | 413 | -20.4937 | 92.4921
2005-11-30 | 16:59 | 21 | 10 | -33.4 | 67 | 409 | 688.7 | 410 | -20.5875 | 91.7728
2005-11-30 | 17:59 | 24 | 9.6 | -33.2 | 68 | 411 | 689.2 | 410 | -20.3875 | 91.8739
2005-11-30 | 18:59 | 24 | 9.6 | -33 | 69 | 396 | 689.5 | 412 | -20.125 | 92.4553
2005-11-30 | 19:59 | 25 | 9.7 | -33 | 69 | 390 | 689.8 | 409 | -20.2188 | 91.7348
2005-11-30 | 20:59 | 41 | 7.7 | -32.9 | 69 | 417 | 690.1 | 398 | -20.4625 | 89.1481
2005-11-30 | 21:59 | 42 | 9 | -32.8 | 69 | 419 | 690.3 | 414 | -19.8625 | 93.038
2005-11-30 | 22:59 | 32 | 10.5 | -32.3 | 69 | 436 | 690.3 | 411 | -19.4563 | 92.5695
2005-11-30 | 23:58 | 31 | 10.8 | -32.6 | 69 | 435 | 690.4 | 423 | -19.3813 | 95.3113
2005-12-01 | 0:59 | 50 | 10.7 | -29.7 | 67 | 436 | 689.1 | 433 | -16.1687 | 99.2783
2005-12-01 | 1:59 | 55 | 9.1 | -30.1 | 67 | 441 | 688.9 | 439 | -16.3813 | 100.539
2005-12-01 | 2:59 | 56 | 9.7 | -29.9 | 67 | 445 | 688.7 | 443 | -16.0562 | 101.6325
2005-12-01 | 3:59 | 36 | 13.1 | -29.2 | 67 | 448 | 688.5 | 444 | -15.325 | 102.2619
2005-12-01 | 4:59 | 34 | 12.8 | -29 | 66 | 450 | 688.3 | 449 | -14.9688 | 103.6106
2005-12-01 | 5:59 | 39 | 11.8 | -29 | 66 | 453 | 688.1 | 316 | -19.125 | 71.3016
2005-12-01 | 6:59 | 34 | 12.8 | -29 | 66 | 441 | 688.2 | 453 | -14.8438 | 104.6034
2005-12-01 | 7:59 | 18 | 14 | -28.4 | 67 | 326 | 688.2 | 394 | -16.0875 | 90.3758
2005-12-01 | 8:59 | 12 | 12.9 | -27.3 | 72 | 457 | 688.2 | 330 | -16.9875 | 75.3296
2005-12-01 | 9:59 | 19 | 12.6 | -27.6 | 68 | 393 | 688.1 | 392 | -15.35 | 90.2732
2005-12-01 | 10:59 | 15 | 14.8 | -27.4 | 67 | 348 | 688.1 | 372 | -15.775 | 85.4727
2005-12-01 | 11:59 | 22 | 10.2 | -28.2 | 67 | 428 | 688.1 | 411 | -15.3562 | 94.6455
2005-12-01 | 12:59 | 32 | 11.6 | -28.7 | 68 | 423 | 688.1 | 425 | -15.4187 | 97.8367
2005-12-01 | 13:59 | 37 | 11 | -28.6 | 68 | 424 | 687.7 | 420 | -15.475 | 96.6566
2005-12-01 | 14:59 | 49 | 10.7 | -28 | 68 | 383 | 687.7 | 389 | -15.8438 | 89.3457
2005-12-01 | 15:59 | 42 | 13.7 | -27.2 | 70 | 333 | 687.1 | 375 | -15.4812 | 86.2977
2005-12-01 | 16:59 | 52 | 14.3 | -25.9 | 69 | 312 | 686.8 | 315 | -16.0562 | 72.2669
2005-12-01 | 17:59 | 68 | 9.2 | -27.6 | 68 | 411 | 686.6 | 405 | -14.9437 | 93.4697
2005-12-01 | 18:59 | 60 | 13 | -27.8 | 68 | 413 | 686.2 | 413 | -14.8938 | 95.3414
2005-12-01 | 19:59 | 51 | 13.4 | -27.2 | 68 | 414 | 686 | 413 | -14.2937 | 95.6467
2005-12-01 | 20:59 | 51 | 12.1 | -27.2 | 68 | 417 | 685.9 | 406 | -14.5125 | 93.9162
2005-12-01 | 21:59 | 45 | 15.4 | -27 | 68 | 422 | 685.6 | 420 | -13.875 | 97.4845
2005-12-01 | 22:59 | 45 | 15.6 | -27 | 68 | 427 | 685.3 | 425 | -13.7188 | 98.7269
2005-12-01 | 23:59 | 48 | 17.6 | -26.9 | 68 | 427 | 685 | 427 | -13.5563 | 99.2769
2005-12-02 | 0:59 | 47 | 17.2 | -27 | 68 | 424 | 684.9 | 430 | -13.5625 | 99.9711
2005-12-02 | 1:59 | 41 | 18.1 | -26.9 | 68 | 459 | 684.7 | 442 | -13.0875 | 103.0197
2005-12-02 | 2:59 | 44 | 15.5 | -27.3 | 67 | 441 | 684.6 | 451 | -13.2063 | 105.0514
2005-12-02 | 3:59 | 42 | 16.3 | -27.4 | 68 | 446 | 684.5 | 443 | -13.5563 | 102.9969
2005-12-02 | 4:59 | 42 | 17.1 | -27.4 | 67 | 449 | 684.2 | 448 | -13.4 | 104.2457
2005-12-02 | 5:59 | 39 | 19.3 | -27.2 | 68 | 364 | 684.1 | 331 | -16.8562 | 75.6114
2005-12-02 | 6:59 | 38 | 16.7 | -27.1 | 67 | 392 | 684.1 | 399 | -14.6312 | 92.2385
2005-12-02 | 7:59 | 44 | 12.3 | -27.3 | 67 | 329 | 684.1 | 409 | -14.5188 | 94.607
2005-12-02 | 8:59 | 31 | 14.3 | -27.1 | 68 | 368 | 683.9 | 394 | -14.7875 | 91.0068
2005-12-02 | 9:59 | 28 | 13.1 | -27.1 | 67 | 460 | 683.9 | 381 | -15.1937 | 87.8134
2005-12-02 | 10:59 | 26 | 14.8 | -27.8 | 67 | 420 | 683.8 | 436 | -14.175 | 101.0371
2005-12-02 | 11:59 | 28 | 12.9 | -27.7 | 67 | 400 | 683.9 | 415 | -14.7312 | 95.8862
2005-12-02 | 12:59 | 19 | 11.7 | -27.5 | 67 | 380 | 683.6 | 364 | -16.125 | 83.4776
2005-12-02 | 13:59 | 16 | 10.9 | -27.1 | 67 | 424 | 683.7 | 415 | -14.1312 | 96.193
2005-12-02 | 14:59 | 18 | 14.6 | -27.6 | 68 | 359 | 683.6 | 349 | -16.6938 | 79.793
2005-12-02 | 15:59 | 17 | 13.3 | -27.5 | 68 | 374 | 683.6 | 382 | -15.5625 | 87.8703
2005-12-02 | 16:59 | 14 | 11.2 | -27.4 | 68 | 398 | 683.8 | 383 | -15.4313 | 88.1623
2005-12-02 | 17:59 | 13 | 12.2 | -27.5 | 68 | 367 | 684 | 384 | -15.5 | 88.3599
2005-12-02 | 18:59 | 4 | 13.1 | -27.1 | 69 | 427 | 684.2 | 375 | -15.3812 | 86.3439
2005-12-02 | 19:59 | 4 | 10.2 | -27.7 | 68 | 439 | 684.5 | 367 | -16.2312 | 84.1175
2005-12-02 | 20:59 | 0 | 9.7 | -28.8 | 68 | 426 | 684.8 | 379 | -16.9563 | 86.5295
2005-12-02 | 21:59 | 5 | 12.2 | -29.5 | 70 | 423 | 685 | 426 | -16.1875 | 97.6635
2005-12-02 | 22:59 | 9 | 12.2 | -29.7 | 69 | 420 | 685.3 | 426 | -16.3875 | 97.5585
2005-12-02 | 23:59 | 11 | 12.7 | -29.8 | 67 | 442 | 685.6 | 434 | -16.2375 | 99.4708
2005-12-03 | 0:59 | 3 | 13.1 | -30.6 | 66 | 443 | 685.9 | 442 | -16.7875 | 101.0049
2005-12-03 | 1:59 | 341 | 10 | -29.5 | 67 | 424 | 686.3 | 418 | -16.4375 | 95.7007
2005-12-03 | 2:59 | 345 | 10.5 | -29.8 | 66 | 460 | 686.6 | 424 | -16.55 | 97.0156
2005-12-03 | 3:59 | 339 | 8.1 | -30.2 | 66 | 460 | 686.9 | 442 | -16.3875 | 101.2227
2005-12-03 | 4:59 | 353 | 8.4 | -31.1 | 66 | 454 | 687.3 | 457 | -16.8188 | 104.415
2005-12-03 | 5:59 | 352 | 9.1 | -31.8 | 67 | 458 | 687.4 | 320 | -21.8 | 71.1496
2005-12-03 | 6:59 | 343 | 6.6 | -32.1 | 67 | 459 | 687.8 | 459 | -17.7563 | 104.3419
2005-12-03 | 7:59 | 345 | 4.5 | -32.6 | 67 | 456 | 687.9 | 457 | -18.3188 | 103.5705
2005-12-03 | 8:59 | 13 | 5.1 | -32.6 | 68 | 453 | 688.1 | 451 | -18.5063 | 102.1065
2005-12-03 | 9:59 | 286 | 0 | -32.8 | 70 | 450 | 688 | 451 | -18.7063 | 101.9954
2005-12-03 | 10:59 | 88 | 5.3 | -33.2 | 66 | 443 | 688.1 | 447 | -19.2312 | 100.8017
2005-12-03 | 11:59 | 152 | 3 | -33.3 | 66 | 438 | 688.1 | 441 | -19.5188 | 99.2924
2005-12-03 | 12:59 | 154 | 3.1 | -33.9 | 66 | 432 | 688 | 435 | -20.3062 | 97.5195
2005-12-03 | 13:59 | 160 | 5.6 | -33.5 | 66 | 427 | 688 | 429 | -20.0938 | 96.2867
2005-12-03 | 14:59 | 156 | 7.1 | -33.6 | 66 | 422 | 688.1 | 424 | -20.35 | 95.0306
2005-12-03 | 15:59 | 153 | 6.5 | -34 | 65 | 419 | 688.1 | 420 | -20.875 | 93.8624
2005-12-03 | 16:59 | 158 | 5.7 | -33.9 | 65 | 417 | 688.1 | 418 | -20.8375 | 93.4348
2005-12-03 | 17:59 | 157 | 4.9 | -34 | 65 | 418 | 688 | 418 | -20.9375 | 93.3833
2005-12-03 | 18:59 | 192 | 6 | -34 | 65 | 422 | 688.1 | 421 | -20.8438 | 94.1021
2005-12-03 | 19:59 | 157 | 4.6 | -34.1 | 65 | 421 | 688.2 | 420 | -20.975 | 93.8107
2005-12-03 | 20:59 | 171 | 7 | -34.3 | 65 | 423 | 688.2 | 413 | -21.3938 | 92.0341
2005-12-03 | 21:59 | 189 | 5.8 | -34.5 | 65 | 428 | 688.4 | 425 | -21.2188 | 94.7999
2005-12-03 | 22:59 | 186 | 7.3 | -34.2 | 65 | 433 | 688.5 | 430 | -20.7625 | 96.1569
2005-12-03 | 23:59 | 189 | 7 | -34.4 | 64 | 438 | 688.4 | 436 | -20.775 | 97.4919
2005-12-04 | 0:59 | 189 | 7.3 | -34.1 | 64 | 444 | 688.4 | 441 | -20.3188 | 98.8578
2005-12-04 | 1:59 | 182 | 8 | -34.2 | 64 | 450 | 688.6 | 447 | -20.2312 | 100.251
2005-12-04 | 2:59 | 167 | 8.4 | -34.1 | 63 | 454 | 688.5 | 452 | -19.975 | 101.515
2005-12-04 | 3:59 | 178 | 8.7 | -33.9 | 65 | 457 | 688.4 | 453 | -19.7437 | 101.8687
2005-12-04 | 4:59 | 170 | 8.8 | -33.8 | 64 | 459 | 688.3 | 458 | -19.4875 | 103.1377
2005-12-04 | 5:59 | 178 | 8.1 | -33.6 | 64 | 460 | 688.3 | 331 | -23.2563 | 73.0015
2005-12-04 | 6:59 | 167 | 7.8 | -33.4 | 64 | 461 | 688.3 | 461 | -18.9937 | 104.0937
2005-12-04 | 7:59 | 163 | 8.4 | -33.5 | 63 | 458 | 688.3 | 459 | -19.1562 | 103.5502
2005-12-04 | 8:59 | 162 | 8.8 | -33.4 | 62 | 455 | 688.1 | 453 | -19.2437 | 102.1477
2005-12-04 | 9:59 | 171 | 9.4 | -33.2 | 62 | 450 | 688 | 452 | -19.075 | 102.0162
2005-12-04 | 10:59 | 167 | 11.2 | -33.2 | 62 | 445 | 687.8 | 448 | -19.2 | 101.0444
2005-12-04 | 11:59 | 158 | 11.1 | -32.7 | 62 | 439 | 687.7 | 442 | -18.8875 | 99.8613
2005-12-04 | 12:59 | 146 | 11 | -32.4 | 62 | 433 | 687.7 | 436 | -18.775 | 98.5662
2005-12-04 | 13:59 | 142 | 12.7 | -32.3 | 61 | 428 | 687.5 | 431 | -18.8313 | 97.406
2005-12-04 | 14:59 | 150 | 8.3 | -32.4 | 61 | 423 | 687.4 | 425 | -19.1187 | 95.8994
2005-12-04 | 15:59 | 122 | 11.3 | -32.2 | 60 | 420 | 687.4 | 421 | -19.0437 | 95.0357
2005-12-04 | 16:59 | 120 | 10.4 | -32.4 | 60 | 419 | 687.5 | 419 | -19.3062 | 94.4488
2005-12-04 | 17:59 | 118 | 8.7 | -32.4 | 61 | 421 | 687.5 | 420 | -19.275 | 94.6903
2005-12-04 | 18:59 | 118 | 8.2 | -32.2 | 61 | 424 | 687.8 | 423 | -18.9812 | 95.5198
2005-12-04 | 19:59 | 113 | 7.5 | -31.9 | 61 | 422 | 688 | 422 | -18.7125 | 95.4337
2005-12-04 | 20:59 | 95 | 8.8 | -31.8 | 62 | 424 | 688.2 | 413 | -18.8938 | 93.3062
2005-12-04 | 21:59 | 100 | 8 | -31.7 | 62 | 429 | 688.4 | 426 | -18.3875 | 96.5089
2005-12-04 | 22:59 | 105 | 6.4 | -31.4 | 62 | 434 | 688.5 | 432 | -17.9 | 98.1276
2005-12-04 | 23:59 | 111 | 7.3 | -31.5 | 61 | 439 | 688.7 | 437 | -17.8438 | 99.2936
2005-12-05 | 0:59 | 95 | 7.9 | -31.4 | 62 | 445 | 688.7 | 442 | -17.5875 | 100.5692
2005-12-05 | 1:59 | 87 | 8 | -31.2 | 62 | 451 | 688.7 | 448 | -17.2 | 102.1483
2005-12-05 | 2:59 | 92 | 6.5 | -31.2 | 62 | 456 | 688.7 | 453 | -17.0437 | 103.3756
2005-12-05 | 3:59 | 86 | 8.2 | -31.3 | 63 | 459 | 688.8 | 454 | -17.1125 | 103.5653
2005-12-05 | 4:59 | 89 | 9.2 | -31.3 | 62 | 461 | 688.7 | 460 | -16.925 | 105.0403
2005-12-05 | 5:59 | 92 | 9.9 | -31.2 | 61 | 461 | 688.6 | 330 | -20.8875 | 73.744
2005-12-05 | 6:59 | 93 | 9.9 | -31.3 | 61 | 461 | 688.6 | 461 | -16.8938 | 105.2864
2005-12-05 | 7:59 | 92 | 10.2 | -31.5 | 60 | 461 | 688.6 | 461 | -17.0938 | 105.1728
2005-12-05 | 8:59 | 89 | 10.7 | -31.6 | 59 | 458 | 688.4 | 457 | -17.3188 | 104.1335
2005-12-05 | 9:59 | 92 | 12.3 | -31.6 | 59 | 454 | 688.3 | 457 | -17.3188 | 104.1335
2005-12-05 | 10:59 | 91 | 13.7 | -31.4 | 58 | 449 | 688.2 | 452 | -17.275 | 103.0186
2005-12-05 | 11:59 | 104 | 9.9 | -31.4 | 58 | 444 | 688.1 | 447 | -17.4312 | 101.7929
2005-12-05 | 12:59 | 84 | 13.6 | -31.1 | 59 | 438 | 687.9 | 441 | -17.3188 | 100.4877
2005-12-05 | 13:59 | 86 | 12.9 | -30.9 | 59 | 432 | 687.7 | 435 | -17.3062 | 99.1272
2005-12-05 | 14:59 | 86 | 10.3 | -30.9 | 60 | 428 | 687.6 | 430 | -17.4625 | 97.9051
2005-12-05 | 15:59 | 89 | 9.8 | -30.9 | 61 | 424 | 687.5 | 426 | -17.5875 | 96.9287
2005-12-05 | 16:59 | 87 | 8 | -30.8 | 61 | 422 | 687.6 | 423 | -17.5813 | 96.2494
2005-12-05 | 17:59 | 80 | 10.5 | -30.6 | 61 | 424 | 687.5 | 423 | -17.3813 | 96.3536
2005-12-05 | 18:59 | 82 | 9.1 | -30.5 | 62 | 426 | 687.6 | 426 | -17.1875 | 97.1386
2005-12-05 | 19:59 | 72 | 10.4 | -30 | 62 | 425 | 687.6 | 425 | -16.7188 | 97.1561
2005-12-05 | 20:59 | 69 | 10 | -30 | 63 | 427 | 687.7 | 417 | -16.9688 | 95.1988
2005-12-05 | 21:59 | 68 | 9.2 | -30.1 | 63 | 432 | 687.7 | 429 | -16.6938 | 98.0837
2005-12-05 | 22:59 | 69 | 9.9 | -30.1 | 62 | 437 | 687.8 | 435 | -16.5063 | 99.556
2005-12-05 | 23:59 | 65 | 10.3 | -30.2 | 62 | 443 | 687.8 | 440 | -16.45 | 100.7308
2005-12-06 | 0:59 | 69 | 9.6 | -30.3 | 63 | 449 | 687.8 | 446 | -16.3625 | 102.1525
2005-12-06 | 1:59 | 64 | 9.9 | -30.1 | 63 | 454 | 687.6 | 451 | -16.0063 | 103.4956
2005-12-06 | 2:59 | 66 | 9.5 | -30.1 | 62 | 458 | 687.6 | 456 | -15.85 | 104.7308
2005-12-06 | 3:59 | 62 | 9.3 | -30.1 | 63 | 461 | 687.6 | 457 | -15.8187 | 104.9781
2005-12-06 | 4:59 | 71 | 11.2 | -30.1 | 62 | 461 | 687.5 | 461 | -15.6937 | 105.9679
2005-12-06 | 5:59 | 73 | 11.7 | -30.1 | 62 | 461 | 687.4 | 328 | -19.85 | 73.7163
2005-12-06 | 6:59 | 67 | 10.6 | -30 | 62 | 461 | 687.4 | 461 | -15.5938 | 106.0247
2005-12-06 | 7:59 | 75 | 10.6 | -29.9 | 61 | 461 | 687.3 | 461 | -15.4938 | 106.0815
2005-12-06 | 8:59 | 76 | 11.5 | -30.2 | 61 | 459 | 687.1 | 457 | -15.9187 | 104.9218
2005-12-06 | 9:59 | 84 | 10.3 | -30.4 | 61 | 456 | 687 | 458 | -16.0875 | 105.0561
2005-12-06 | 10:59 | 86 | 9.4 | -30.6 | 61 | 450 | 686.8 | 453 | -16.4438 | 103.7104
2005-12-06 | 11:59 | 90 | 8.7 | -30.5 | 61 | 444 | 686.4 | 448 | -16.5 | 102.5347
2005-12-06 | 12:59 | 81 | 9.9 | -30.4 | 61 | 439 | 686 | 442 | -16.5875 | 101.1138
2005-12-06 | 13:59 | 74 | 8.1 | -30.3 | 60 | 433 | 685.7 | 436 | -16.675 | 99.6942
2005-12-06 | 14:59 | 77 | 8.9 | -30.4 | 61 | 429 | 685.2 | 431 | -16.9312 | 98.4148
2005-12-06 | 15:59 | 77 | 7.5 | -30.4 | 63 | 425 | 684.9 | 427 | -17.0562 | 97.4357
2005-12-06 | 16:59 | 76 | 8.4 | -30.1 | 63 | 423 | 684.7 | 424 | -16.85 | 96.8589
2005-12-06 | 17:59 | 65 | 9.3 | -29.8 | 64 | 425 | 684.6 | 424 | -16.55 | 97.0156
2005-12-06 | 18:59 | 62 | 9.5 | -29.8 | 64 | 429 | 684.5 | 428 | -16.425 | 97.9968
2005-12-06 | 19:59 | 51 | 11.3 | -29.6 | 65 | 427 | 684.4 | 427 | -16.2563 | 97.8566
2005-12-06 | 20:59 | 55 | 12.2 | -29.8 | 66 | 430 | 684.5 | 419 | -16.7063 | 95.7909
2005-12-06 | 21:59 | 58 | 10.7 | -30.2 | 66 | 435 | 684.5 | 432 | -16.7 | 98.7663
2005-12-06 | 22:59 | 57 | 10.7 | -30 | 65 | 440 | 684.5 | 437 | -16.3438 | 100.1012
2005-12-06 | 23:59 | 61 | 9.5 | -29.6 | 65 | 445 | 684.5 | 443 | -15.7562 | 101.7962
2005-12-07 | 0:59 | 49 | 11.9 | -29.6 | 65 | 451 | 684.5 | 448 | -15.6 | 103.0314
2005-12-07 | 1:59 | 49 | 10.3 | -29.6 | 65 | 457 | 684.2 | 454 | -15.4125 | 104.5162
2005-12-07 | 2:59 | 47 | 12.7 | -29.5 | 65 | 461 | 684.2 | 459 | -15.1562 | 105.8121
2005-12-07 | 3:59 | 42 | 10.9 | -29.5 | 67 | 461 | 684.2 | 458 | -15.1875 | 105.564
2005-12-07 | 4:59 | 50 | 12.3 | -29.4 | 66 | 461 | 684.2 | 461 | -14.9938 | 106.3655
2005-12-07 | 5:59 | 54 | 10.3 | -29.4 | 66 | 461 | 684.2 | 332 | -19.025 | 74.9527
2005-12-07 | 6:59 | 64 | 9.7 | -29.5 | 65 | 461 | 684.2 | 461 | -15.0938 | 106.3087
2005-12-07 | 7:59 | 62 | 9.9 | -29.5 | 65 | 461 | 684 | 461 | -15.0938 | 106.3087
2005-12-07 | 8:59 | 64 | 9.3 | -29.5 | 65 | 461 | 683.8 | 458 | -15.1875 | 105.564
2005-12-07 | 9:59 | 67 | 9.9 | -29.6 | 64 | 456 | 683.5 | 459 | -15.2562 | 105.7556
2005-12-07 | 10:59 | 77 | 9.6 | -29.5 | 64 | 451 | 683.2 | 454 | -15.3125 | 104.5721
2005-12-07 | 11:59 | 82 | 8.3 | -29.7 | 64 | 446 | 683 | 449 | -15.6687 | 103.2233
2005-12-07 | 12:59 | 79 | 8.3 | -29.8 | 63 | 441 | 682.5 | 443 | -15.9563 | 101.6871
2005-12-07 | 13:59 | 84 | 9.4 | -30.2 | 63 | 436 | 682.1 | 439 | -16.4812 | 100.4849
2005-12-07 | 14:59 | 80 | 8.4 | -30.1 | 63 | 346 | 681.7 | 430 | -16.6625 | 98.3289
2005-12-07 | 15:59 | 93 | 6.4 | -30.1 | 64 | 398 | 681.4 | 430 | -16.6625 | 98.3289
2005-12-07 | 16:59 | 84 | 7.6 | -30.2 | 64 | 398 | 681.2 | 425 | -16.9187 | 97.0513
2005-12-07 | 17:59 | 72 | 5.6 | -29.9 | 65 | 461 | 681.1 | 420 | -16.775 | 95.9839
2005-12-07 | 18:59 | 49 | 7.4 | -29.7 | 66 | 408 | 681.1 | 388 | -17.575 | 88.2885
2005-12-07 | 19:59 | 39 | 8.8 | -29.5 | 66 | 426 | 681.2 | 419 | -16.4062 | 95.9458
2005-12-07 | 20:59 | 26 | 9 | -29 | 67 | 425 | 681.3 | 417 | -15.9688 | 95.7126
2005-12-07 | 21:59 | 29 | 10.9 | -29.6 | 67 | 439 | 681.6 | 416 | -16.6 | 95.1595
2005-12-07 | 22:59 | 17 | 9.8 | -29.9 | 67 | 444 | 681.9 | 434 | -16.3375 | 99.4173
2005-12-07 | 23:59 | 12 | 10.2 | -29.6 | 67 | 439 | 682.1 | 430 | -16.1625 | 98.5938
2005-12-08 | 0:59 | 11 | 12.1 | -30 | 66 | 345 | 682.4 | 428 | -16.625 | 97.8913
2005-12-08 | 1:59 | 1 | 13.3 | -29.8 | 66 | 455 | 682.7 | 447 | -15.8313 | 102.6741
2005-12-08 | 2:59 | 4 | 10.8 | -29.9 | 66 | 409 | 683 | 442 | -16.0875 | 101.386
2005-12-08 | 3:59 | 12 | 11.4 | -30 | 66 | 387 | 683.4 | 390 | -17.8125 | 88.6295
2005-12-08 | 4:59 | 15 | 10 | -30.2 | 65 | 459 | 683.8 | 432 | -16.7 | 98.7663
2005-12-08 | 5:59 | 12 | 9.9 | -30.5 | 65 | 454 | 684.1 | 331 | -20.1562 | 74.2656
2005-12-08 | 6:59 | 10 | 10.6 | -30.5 | 65 | 461 | 684.5 | 461 | -16.0938 | 105.7407
2005-12-08 | 7:59 | 13 | 10.7 | -30.4 | 65 | 461 | 684.8 | 459 | -16.0562 | 105.3032
2005-12-08 | 8:59 | 17 | 10.3 | -30.1 | 65 | 461 | 684.9 | 454 | -15.9125 | 104.2365
2005-12-08 | 9:59 | 18 | 9.8 | -30 | 65 | 424 | 685.2 | 457 | -15.7188 | 105.0344
2005-12-08 | 10:59 | 11 | 10.3 | -29.3 | 66 | 455 | 685.5 | 429 | -15.8938 | 98.5065
2005-12-08 | 11:59 | 12 | 10 | -29.4 | 66 | 459 | 685.8 | 449 | -15.3688 | 103.3893
2005-12-08 | 12:59 | 9 | 10.4 | -29.1 | 66 | 448 | 685.9 | 436 | -15.475 | 100.3388
2005-12-08 | 13:59 | 7 | 11.2 | -29 | 66 | 438 | 686.1 | 434 | -15.4375 | 99.8986
2005-12-08 | 14:59 | 5 | 9.3 | -29.2 | 66 | 432 | 686.2 | 434 | -15.6375 | 99.7916
2005-12-08 | 15:59 | 8 | 9.3 | -29.1 | 68 | 429 | 686.4 | 430 | -15.6625 | 98.8586
2005-12-08 | 16:59 | 10 | 9.9 | -28.9 | 68 | 427 | 686.7 | 428 | -15.525 | 98.4713
2005-12-08 | 17:59 | 10 | 9.4 | -28.9 | 68 | 429 | 686.8 | 429 | -15.4938 | 98.7179
2005-12-08 | 18:59 | 8 | 10.4 | -29.1 | 68 | 434 | 686.9 | 431 | -15.6312 | 99.1051
2005-12-08 | 19:59 | 15 | 10.5 | -29.1 | 69 | 433 | 686.9 | 431 | -15.6312 | 99.1051
2005-12-08 | 20:59 | 18 | 10.6 | -29.2 | 69 | 435 | 686.9 | 422 | -16.0125 | 96.8374
2005-12-08 | 21:59 | 23 | 10.9 | -28.6 | 69 | 354 | 686.9 | 426 | -15.2875 | 98.1358
2005-12-08 | 22:59 | 26 | 8.7 | -28.4 | 69 | 443 | 687 | 424 | -15.15 | 97.7469
2005-12-08 | 23:59 | 33 | 7.5 | -28.7 | 68 | 436 | 686.9 | 412 | -15.825 | 94.6379
2005-12-09 | 0:59 | 22 | 7.9 | -27.4 | 69 | 340 | 686.8 | 426 | -14.0875 | 98.7656
2005-12-09 | 1:59 | 9 | 9.1 | -27.2 | 69 | 446 | 686.7 | 416 | -14.2 | 96.3895
2005-12-09 | 2:59 | 13 | 8.7 | -28 | 69 | 461 | 686.5 | 421 | -14.8438 | 97.2142
2005-12-09 | 3:59 | 18 | 8.7 | -28.2 | 69 | 286 | 686.5 | 430 | -14.7625 | 99.3354
2005-12-09 | 4:59 | 12 | 8.6 | -28.1 | 69 | 461 | 686.5 | 438 | -14.4125 | 101.3724
2005-12-09 | 5:59 | 14 | 7.5 | -27.7 | 68 | 354 | 686.6 | 335 | -17.2312 | 76.3703
2005-12-09 | 6:59 | 14 | 9 | -27.1 | 69 | 461 | 686.6 | 393 | -14.8187 | 90.7607
2005-12-09 | 7:59 | 14 | 8.6 | -27.2 | 68 | 461 | 686.4 | 430 | -13.7625 | 99.8652
2005-12-09 | 8:59 | 29 | 9.6 | -27.8 | 68 | 426 | 686.5 | 430 | -14.3625 | 99.5473
2005-12-09 | 9:59 | 22 | 9.6 | -27.9 | 67 | 425 | 686.4 | 433 | -14.3688 | 100.2385
2005-12-09 | 10:59 | 21 | 9.5 | -27.3 | 67 | 461 | 686.2 | 433 | -13.7688 | 100.5586
2005-12-09 | 11:59 | 36 | 9.3 | -27.7 | 67 | 406 | 686.2 | 440 | -13.95 | 102.086
2005-12-09 | 12:59 | 23 | 9.8 | -27.3 | 68 | 417 | 686 | 388 | -15.175 | 89.4357
2005-12-09 | 13:59 | 12 | 9.6 | -26.9 | 69 | 333 | 685.8 | 361 | -15.6188 | 83.0147
2005-12-09 | 14:59 | 13 | 11.8 | -26.5 | 69 | 386 | 685.6 | 364 | -15.125 | 83.926
2005-12-09 | 15:59 | 29 | 9.2 | -27 | 69 | 320 | 685.5 | 347 | -16.1562 | 79.5655
2005-12-09 | 16:59 | 30 | 12.1 | -26.1 | 69 | 365 | 685.3 | 336 | -15.6 | 77.2735
2005-12-09 | 17:59 | 35 | 10.5 | -26.4 | 68 | 412 | 685.1 | 376 | -14.65 | 86.9129
2005-12-09 | 18:59 | 38 | 12.2 | -26.6 | 68 | 400 | 685 | 430 | -13.1625 | 100.183
2005-12-09 | 19:59 | 45 | 10 | -26.9 | 68 | 411 | 684.9 | 387 | -14.8063 | 89.381
2005-12-09 | 20:59 | 50 | 10.3 | -27.4 | 68 | 454 | 684.7 | 410 | -14.5875 | 94.8036
2005-12-09 | 21:59 | 49 | 9 | -28.3 | 68 | 345 | 684.6 | 389 | -16.1438 | 89.2019
2005-12-09 | 22:59 | 41 | 9.6 | -27.8 | 68 | 432 | 684.4 | 383 | -15.8313 | 87.9735
2005-12-09 | 23:59 | 52 | 8 | -28.3 | 67 | 425 | 684.2 | 426 | -14.9875 | 98.2933
2005-12-10 | 0:59 | 55 | 7.4 | -28.7 | 66 | 457 | 684 | 456 | -14.45 | 105.5173
2005-12-10 | 1:59 | 59 | 9.8 | -28.6 | 66 | 461 | 683.6 | 459 | -14.2562 | 106.3211
2005-12-10 | 2:59 | 56 | 10.5 | -28.4 | 65 | 461 | 683.2 | 461 | -13.9938 | 106.9334
2005-12-10 | 3:59 | 65 | 8.8 | -28.7 | 66 | 461 | 683 | 458 | -14.3875 | 106.0154
2005-12-10 | 4:59 | 71 | 9.6 | -28.9 | 64 | 461 | 682.9 | 461 | -14.4938 | 106.6494
2005-12-10 | 5:59 | 71 | 9.8 | -28.8 | 64 | 461 | 682.7 | 331 | -18.4563 | 74.9589
2005-12-10 | 6:59 | 65 | 9.6 | -28.9 | 64 | 461 | 682.5 | 461 | -14.4938 | 106.6494
2005-12-10 | 7:59 | 72 | 10.5 | -28.8 | 64 | 461 | 682.3 | 461 | -14.3938 | 106.7062
2005-12-10 | 8:59 | 69 | 9.5 | -28.9 | 64 | 461 | 682.1 | 457 | -14.6188 | 105.6537
2005-12-10 | 9:59 | 71 | 7.8 | -28.6 | 65 | 461 | 681.8 | 461 | -14.1937 | 106.8198
2005-12-10 | 10:59 | 51 | 10.6 | -28.3 | 65 | 457 | 681.8 | 460 | -13.925 | 106.7404
2005-12-10 | 11:59 | 59 | 10.4 | -28.2 | 65 | 451 | 681.6 | 454 | -14.0125 | 105.2992
2005-12-10 | 12:59 | 56 | 9.9 | -28.5 | 65 | 446 | 681.5 | 448 | -14.5 | 103.6385
2005-12-10 | 13:59 | 48 | 9.1 | -28.6 | 66 | 441 | 681.2 | 443 | -14.7562 | 102.342
2005-12-10 | 14:59 | 58 | 10.1 | -28.6 | 66 | 437 | 681 | 439 | -14.8812 | 101.3503
2005-12-10 | 15:59 | 58 | 9.9 | -28.6 | 67 | 433 | 680.9 | 435 | -15.0062 | 100.3599
2005-12-10 | 16:59 | 59 | 8 | -28.7 | 67 | 431 | 680.9 | 432 | -15.2 | 99.5646
2005-12-10 | 17:59 | 49 | 9.9 | -28.5 | 68 | 433 | 680.8 | 432 | -15 | 99.671
2005-12-10 | 18:59 | 57 | 8.8 | -28.9 | 68 | 440 | 680.7 | 436 | -15.275 | 100.4462
2005-12-10 | 19:59 | 52 | 8.9 | -28.6 | 68 | 436 | 680.6 | 436 | -14.975 | 100.6073
2005-12-10 | 20:59 | 46 | 9.4 | -28.8 | 69 | 438 | 680.6 | 427 | -15.4563 | 98.2774
2005-12-10 | 21:59 | 56 | 8.7 | -29 | 69 | 442 | 680.5 | 440 | -15.25 | 101.3813
2005-12-10 | 22:59 | 54 | 7.6 | -29.1 | 68 | 447 | 680.4 | 445 | -15.1937 | 102.5642
2005-12-10 | 23:59 | 59 | 7.6 | -29 | 68 | 453 | 680.4 | 449 | -14.9688 | 103.6106
2005-12-11 | 0:59 | 46 | 7.6 | -28.8 | 69 | 459 | 680.4 | 456 | -14.55 | 105.4611
2005-12-11 | 1:59 | 51 | 6.8 | -29.1 | 68 | 461 | 680.5 | 461 | -14.6937 | 106.5359
2005-12-11 | 2:59 | 58 | 7.6 | -28.9 | 68 | 461 | 680.4 | 461 | -14.4938 | 106.6494
2005-12-11 | 3:59 | 44 | 7.1 | -28.9 | 69 | 461 | 680.2 | 458 | -14.5875 | 105.9025
2005-12-11 | 4:59 | 58 | 4.8 | -29.2 | 68 | 461 | 680.2 | 461 | -14.7937 | 106.4791
2005-12-11 | 5:59 | 58 | 6.5 | -28.9 | 68 | 461 | 680.2 | 329 | -18.6187 | 74.4401
2005-12-11 | 6:59 | 47 | 6.6 | -28.8 | 68 | 461 | 680.3 | 461 | -14.3938 | 106.7062
2005-12-11 | 7:59 | 53 | 5.6 | -29 | 67 | 461 | 680.3 | 460 | -14.625 | 106.3437
2005-12-11 | 8:59 | 50 | 6 | -29.1 | 67 | 461 | 680.3 | 458 | -14.7875 | 105.7897
2005-12-11 | 9:59 | 57 | 5.1 | -29.3 | 67 | 461 | 680.4 | 461 | -14.8938 | 106.4223
2005-12-11 | 10:59 | 60 | 4.4 | -29.6 | 67 | 461 | 680.5 | 461 | -15.1937 | 106.2519
2005-12-11 | 11:59 | 52 | 5.6 | -29.7 | 67 | 455 | 680.4 | 458 | -15.3875 | 105.4511
2005-12-11 | 12:59 | 44 | 5.7 | -29 | 68 | 449 | 680.5 | 452 | -14.875 | 104.355
2005-12-11 | 13:59 | 30 | 7.2 | -28.4 | 68 | 444 | 680.4 | 447 | -14.4313 | 103.4451
2005-12-11 | 14:59 | 31 | 7.9 | -28.3 | 68 | 440 | 680.4 | 442 | -14.4875 | 102.2573
2005-12-11 | 15:59 | 28 | 7.9 | -28.2 | 69 | 436 | 680.4 | 438 | -14.5125 | 101.3184
2005-12-11 | 16:59 | 22 | 7.6 | -28.2 | 69 | 434 | 680.6 | 435 | -14.6062 | 100.5742
2005-12-11 | 17:59 | 35 | 6.2 | -28.4 | 70 | 436 | 680.8 | 435 | -14.8063 | 100.467
2005-12-11 | 18:59 | 22 | 6 | -28.4 | 70 | 444 | 680.8 | 439 | -14.6813 | 101.4585
2005-12-11 | 19:59 | 9 | 6.6 | -27.7 | 71 | 398 | 680.9 | 429 | -14.2937 | 99.3522
2005-12-11 | 20:59 | 0 | 7.7 | -27.4 | 73 | 364 | 681 | 383 | -15.4313 | 88.1623
2005-12-11 | 21:59 | 20 | 6.1 | -27.5 | 72 | 365 | 681.2 | 383 | -15.5312 | 88.1151
2005-12-11 | 22:59 | 14 | 6.6 | -27.3 | 72 | 356 | 681.2 | 373 | -15.6438 | 85.7627
2005-12-11 | 23:59 | 1 | 6.7 | -27.4 | 71 | 413 | 681.3 | 416 | -14.4 | 96.287
2005-12-12 | 0:59 | 0 | 4.6 | -27.8 | 71 | 364 | 681.6 | 349 | -16.8938 | 79.707
2005-12-12 | 1:59 | 2 | 8.7 | -28.6 | 71 | 326 | 681.6 | 329 | -18.3188 | 74.5617
2005-12-12 | 2:59 | 329 | 2.9 | -28.6 | 70 | 327 | 681.7 | 322 | -18.5375 | 72.8885
2005-12-12 | 3:59 | 0 | 4.7 | -28.5 | 70 | 328 | 681.7 | 316 | -18.625 | 71.4963
2005-12-12 | 4:59 | 350 | 7.1 | -28.8 | 70 | 304 | 681.8 | 318 | -18.8625 | 71.8557
2005-12-12 | 5:59 | 1 | 6.5 | -28.8 | 70 | 325 | 682 | 316 | -18.925 | 71.3795
2005-12-12 | 6:59 | 344 | 6 | -28.7 | 70 | 312 | 682 | 318 | -18.7625 | 71.8949
2005-12-12 | 7:59 | 333 | 6.7 | -28.9 | 70 | 304 | 682 | 318 | -18.9625 | 71.8165
2005-12-12 | 8:59 | 308 | 4.6 | -29 | 70 | 307 | 682 | 311 | -19.2812 | 70.1136
2005-12-12 | 9:59 | 25 | 6.6 | -28.7 | 70 | 327 | 682 | 332 | -18.325 | 75.239
2005-12-12 | 10:59 | 37 | 5.1 | -28.9 | 70 | 403 | 682.1 | 381 | -16.9937 | 86.9685
2005-12-12 | 11:59 | 24 | 7.2 | -29 | 70 | 373 | 682 | 390 | -16.8125 | 89.1099
2005-12-12 | 12:59 | 349 | 7.8 | -29.3 | 70 | 318 | 682 | 353 | -18.2688 | 80.0226
2005-12-12 | 13:59 | 343 | 4 | -29 | 70 | 318 | 681.9 | 337 | -18.4688 | 76.3125
2005-12-12 | 14:59 | 353 | 5.6 | -28.4 | 71 | 320 | 681.8 | 330 | -18.0875 | 74.8823
2005-12-12 | 15:59 | 15 | 5.7 | -27.9 | 70 | 461 | 681.7 | 364 | -16.525 | 83.2982
2005-12-12 | 16:59 | 345 | 9.8 | -27.7 | 71 | 334 | 681.6 | 344 | -16.95 | 78.5413
2005-12-12 | 17:59 | 12 | 7.6 | -27.2 | 72 | 363 | 681.6 | 342 | -16.5125 | 78.269
2005-12-12 | 18:59 | 8 | 9.6 | -27.4 | 71 | 357 | 681.6 | 362 | -16.0875 | 83.0356
2005-12-12 | 19:59 | 6 | 10.1 | -28.4 | 70 | 270 | 681.8 | 339 | -17.8062 | 77.0421
2005-12-12 | 20:59 | 12 | 7.1 | -28.4 | 70 | 445 | 681.9 | 391 | -16.1812 | 89.6425
2005-12-12 | 21:59 | 2 | 5.9 | -28.8 | 70 | 403 | 681.9 | 414 | -15.8625 | 95.0782
2005-12-12 | 22:59 | 10 | 2.5 | -28.6 | 70 | 308 | 681.9 | 382 | -16.6625 | 87.3526
2005-12-12 | 23:59 | 331 | 4.5 | -28.7 | 70 | 349 | 681.9 | 374 | -17.0125 | 85.362
2005-12-13 | 0:59 | 336 | 7.2 | -28.4 | 70 | 357 | 681.9 | 367 | -16.9312 | 83.801
2005-12-13 | 1:59 | 303 | 6.4 | -28 | 71 | 262 | 681.7 | 332 | -17.625 | 75.5254
2005-12-13 | 2:59 | 275 | 3.3 | -27.8 | 71 | 409 | 681.8 | 352 | -16.8 | 80.4328
2005-12-13 | 3:59 | 307 | 1 | -28.3 | 70 | 461 | 681.8 | 432 | -14.8 | 99.7775
2005-12-13 | 4:59 | 30 | 3.6 | -28.7 | 70 | 461 | 681.9 | 398 | -16.2625 | 91.2075
2005-12-13 | 5:59 | 17 | 0 | -29.7 | 68 | 458 | 682.1 | 333 | -19.2937 | 75.0682
2005-12-13 | 6:59 | 15 | 5.7 | -30.4 | 68 | 460 | 682.2 | 459 | -16.0562 | 105.3032
2005-12-13 | 7:59 | 84 | 2.6 | -31 | 68 | 461 | 682.2 | 459 | -16.6562 | 104.9639
2005-12-13 | 8:59 | 79 | 4.6 | -32.1 | 67 | 461 | 682.3 | 458 | -17.7875 | 104.0969
2005-12-13 | 9:59 | 72 | 4.1 | -31.9 | 67 | 461 | 682.5 | 461 | -17.4937 | 104.9456
2005-12-13 | 10:59 | 52 | 3.8 | -31.6 | 67 | 461 | 682.5 | 461 | -17.1938 | 105.116
2005-12-13 | 11:59 | 63 | 2.2 | -32.4 | 66 | 458 | 682.6 | 460 | -18.025 | 104.4169
2005-12-13 | 12:59 | 349 | 0.8 | -32.6 | 66 | 452 | 682.6 | 454 | -18.4125 | 102.8382
2005-12-13 | 13:59 | 335 | 0 | -32.4 | 66 | 421 | 682.7 | 452 | -18.275 | 102.4617
2005-12-13 | 14:59 | 310 | 1.8 | -32.6 | 67 | 461 | 682.7 | 440 | -18.85 | 99.4298
2005-12-13 | 15:59 | 345 | 0 | -32.7 | 66 | 440 | 682.8 | 443 | -18.8562 | 100.1043
2005-12-13 | 16:59 | 292 | 0 | -32.3 | 67 | 438 | 682.8 | 438 | -18.6125 | 99.106
2005-12-13 | 17:59 | 291 | 0 | -31.6 | 68 | 439 | 682.9 | 438 | -17.9125 | 99.4837
2005-12-13 | 18:59 | 344 | 6.1 | -33 | 67 | 444 | 683.2 | 440 | -19.25 | 99.213
2005-12-13 | 19:59 | 7 | 3.8 | -32.7 | 67 | 447 | 683.3 | 440 | -18.95 | 99.3756
2005-12-13 | 20:59 | 14 | 5.5 | -32.7 | 67 | 417 | 683.4 | 417 | -19.6687 | 93.8117
2005-12-13 | 21:59 | 16 | 5.9 | -32.3 | 67 | 458 | 683.5 | 444 | -18.425 | 100.5662
2005-12-13 | 22:59 | 32 | 3.3 | -31.1 | 69 | 353 | 683.7 | 389 | -18.9438 | 87.86
2005-12-13 | 23:59 | 36 | 4.7 | -30.8 | 69 | 372 | 683.7 | 383 | -18.8313 | 86.558
2005-12-14 | 0:59 | 23 | 5.8 | -31 | 69 | 357 | 683.6 | 377 | -19.2188 | 85.022
2005-12-14 | 1:59 | 51 | 3.7 | -32.5 | 67 | 461 | 683.6 | 415 | -19.5312 | 93.4321
2005-12-14 | 2:59 | 44 | 6.4 | -32.1 | 67 | 461 | 683.6 | 461 | -17.6938 | 104.832
2005-12-14 | 3:59 | 45 | 7.6 | -31.9 | 68 | 461 | 683.4 | 458 | -17.5875 | 104.2097
2005-12-14 | 4:59 | 53 | 8.4 | -32.4 | 67 | 461 | 683.4 | 461 | -17.9937 | 104.6616
2005-12-14 | 5:59 | 63 | 7.3 | -32.4 | 67 | 461 | 683.3 | 304 | -22.9 | 67.1801
2005-12-14 | 6:59 | 65 | 8.3 | -32.3 | 67 | 461 | 683.3 | 461 | -17.8938 | 104.7184
2005-12-14 | 7:59 | 59 | 9.1 | -32.1 | 67 | 385 | 683.3 | 439 | -18.3813 | 99.4573
2005-12-14 | 8:59 | 51 | 9.3 | -29 | 70 | 456 | 683 | 384 | -17 | 87.6503
2005-12-14 | 9:59 | 69 | 8.9 | -30.8 | 68 | 461 | 683 | 460 | -16.425 | 105.3236
2005-12-14 | 10:59 | 62 | 8.3 | -31.2 | 68 | 461 | 682.8 | 461 | -16.7937 | 105.3432
2005-12-14 | 11:59 | 63 | 8.2 | -31.1 | 68 | 449 | 682.6 | 458 | -16.7875 | 104.6612
2005-12-14 | 12:59 | 60 | 9.1 | -30.5 | 68 | 457 | 682.3 | 446 | -16.5625 | 102.0426
2005-12-14 | 13:59 | 59 | 10.7 | -30.1 | 68 | 449 | 682.1 | 450 | -16.0375 | 103.2488
2005-12-14 | 14:59 | 61 | 8.5 | -30.4 | 68 | 442 | 681.7 | 445 | -16.4937 | 101.8515
2005-12-14 | 15:59 | 58 | 8.5 | -30 | 68 | 441 | 681.4 | 439 | -16.2812 | 100.5931
2005-12-14 | 16:59 | 50 | 7.1 | -30.2 | 67 | 439 | 681.4 | 434 | -16.6375 | 99.2569
2005-12-14 | 17:59 | 16 | 9.1 | -29.3 | 68 | 437 | 681.4 | 436 | -15.675 | 100.2313
2005-12-14 | 18:59 | 12 | 8.1 | -29.9 | 68 | 445 | 681.5 | 440 | -16.15 | 100.8934
2005-12-14 | 19:59 | 4 | 9.2 | -29.4 | 70 | 411 | 681.6 | 435 | -15.8063 | 99.9311
2005-12-14 | 20:59 | 357 | 6 | -29.3 | 71 | 383 | 681.7 | 393 | -17.0188 | 89.6955
2005-12-14 | 21:59 | 346 | 6.3 | -29.7 | 70 | 379 | 681.9 | 408 | -16.95 | 93.1536
2005-12-14 | 22:59 | 337 | 6.3 | -29.4 | 70 | 428 | 682.1 | 405 | -16.7437 | 92.5715
2005-12-14 | 23:59 | 343 | 7.5 | -28.7 | 71 | 345 | 682 | 383 | -16.7312 | 87.5489
2005-12-15 | 0:59 | 338 | 6.2 | -28.4 | 71 | 330 | 682 | 344 | -17.65 | 78.2446
2005-12-15 | 1:59 | 344 | 7.3 | -27.7 | 71 | 342 | 682 | 331 | -17.3562 | 75.4075
2005-12-15 | 2:59 | 8 | 8.2 | -27.4 | 72 | 352 | 681.9 | 340 | -16.775 | 77.7013
2005-12-15 | 3:59 | 12 | 3.5 | -27.7 | 71 | 341 | 682 | 373 | -16.0437 | 85.5789
2005-12-15 | 4:59 | 38 | 5.3 | -27.5 | 71 | 327 | 682 | 343 | -16.7812 | 78.3842
2005-12-15 | 5:59 | 23 | 6.1 | -27.2 | 72 | 361 | 681.9 | 347 | -16.3562 | 79.48
2005-12-15 | 6:59 | 21 | 7.1 | -27.5 | 71 | 352 | 682.1 | 352 | -16.5 | 80.5629
2005-12-15 | 7:59 | 43 | 6.7 | -27.7 | 71 | 267 | 682.2 | 362 | -16.3875 | 82.9018
2005-12-15 | 8:59 | 15 | 1.9 | -27.2 | 72 | 358 | 682.2 | 341 | -16.5437 | 78.027
2005-12-15 | 9:59 | 34 | 3.9 | -27.3 | 72 | 332 | 682.1 | 360 | -16.05 | 82.5935
2005-12-15 | 10:59 | 45 | 6.9 | -26.7 | 72 | 336 | 682.1 | 345 | -15.9187 | 79.2079
2005-12-15 | 11:59 | 44 | 5.8 | -26.9 | 72 | 361 | 682.2 | 358 | -15.7125 | 82.2835
2005-12-15 | 12:59 | 59 | 6 | -27.1 | 71 | 458 | 682.1 | 401 | -14.5687 | 92.7318
2005-12-15 | 13:59 | 38 | 4.7 | -28.1 | 71 | 380 | 682.2 | 435 | -14.5062 | 100.6278
2005-12-15 | 14:59 | 39 | 5.2 | -27.9 | 70 | 395 | 682.1 | 400 | -15.4 | 92.0909
2005-12-15 | 15:59 | 37 | 4.3 | -27.2 | 71 | 381 | 682.1 | 415 | -14.2312 | 96.1418
2005-12-15 | 16:59 | 28 | 4.5 | -28.3 | 69 | 337 | 682.4 | 361 | -17.0188 | 82.3921
2005-12-15 | 17:59 | 13 | 5.6 | -27.5 | 69 | 459 | 682.7 | 385 | -15.4688 | 88.6049
2005-12-15 | 18:59 | 15 | 5.8 | -27.7 | 70 | 377 | 682.8 | 389 | -15.5437 | 89.4895
2005-12-15 | 19:59 | 43 | 5.1 | -28.7 | 69 | 406 | 683.1 | 410 | -15.8875 | 94.1469
2005-12-15 | 20:59 | 37 | 6.3 | -28.9 | 68 | 445 | 683.2 | 425 | -15.6188 | 97.732
2005-12-15 | 21:59 | 34 | 7.4 | -29.2 | 68 | 425 | 683.4 | 443 | -15.3562 | 102.0145
2005-12-15 | 22:59 | 19 | 7.7 | -28.5 | 69 | 387 | 683.6 | 415 | -15.5312 | 95.4772
2005-12-15 | 23:59 | 30 | 6.1 | -29.6 | 69 | 461 | 683.8 | 405 | -16.9438 | 92.4717
2005-12-16 | 0:59 | 39 | 4.8 | -29.9 | 68 | 461 | 683.8 | 458 | -15.5875 | 105.3383
2005-12-16 | 1:59 | 41 | 8.2 | -29.6 | 68 | 461 | 683.9 | 460 | -15.225 | 106.0037
2005-12-16 | 2:59 | 32 | 7.4 | -30 | 67 | 461 | 683.9 | 461 | -15.5938 | 106.0247
2005-12-16 | 3:59 | 27 | 8.6 | -30.2 | 68 | 461 | 684 | 458 | -15.8875 | 105.169
2005-12-16 | 4:59 | 40 | 5.7 | -30.1 | 67 | 461 | 684 | 461 | -15.6937 | 105.9679
2005-12-16 | 5:59 | 45 | 8.3 | -29.9 | 66 | 461 | 684.2 | 298 | -20.5875 | 66.7032
2005-12-16 | 6:59 | 44 | 7.7 | -30.1 | 65 | 433 | 684.3 | 450 | -16.0375 | 103.2488
2005-12-16 | 7:59 | 43 | 6.6 | -28.5 | 65 | 453 | 684.3 | 382 | -16.5625 | 87.3997
2005-12-16 | 8:59 | 65 | 5.6 | -29.8 | 65 | 461 | 684.3 | 455 | -15.5813 | 104.6518
2005-12-16 | 9:59 | 71 | 5.9 | -30.4 | 65 | 461 | 684.1 | 459 | -16.0562 | 105.3032
2005-12-16 | 10:59 | 75 | 6.5 | -30.5 | 65 | 461 | 684 | 461 | -16.0938 | 105.7407
2005-12-16 | 11:59 | 81 | 6.8 | -31 | 64 | 430 | 683.9 | 459 | -16.6562 | 104.9639
2005-12-16 | 12:59 | 80 | 5.2 | -29.6 | 66 | 447 | 683.7 | 421 | -16.4438 | 96.3843
2005-12-16 | 13:59 | 65 | 5.2 | -28.6 | 66 | 371 | 683.4 | 395 | -16.2563 | 90.5231
2005-12-16 | 14:59 | 28 | 8.1 | -28.5 | 65 | 461 | 683.2 | 399 | -16.0312 | 91.5504
2005-12-16 | 15:59 | 73 | 6.2 | -29.6 | 65 | 441 | 683.1 | 419 | -16.5063 | 95.8941
2005-12-16 | 16:59 | 78 | 6.6 | -30 | 66 | 400 | 682.9 | 415 | -17.0312 | 94.7103
2005-12-16 | 17:59 | 83 | 7.6 | -30.4 | 66 | 440 | 682.8 | 421 | -17.2437 | 95.9693
2005-12-16 | 18:59 | 90 | 7.3 | -30.4 | 65 | 448 | 682.5 | 442 | -16.5875 | 101.1138
2005-12-16 | 19:59 | 96 | 7.8 | -30.3 | 65 | 443 | 682.4 | 443 | -16.4563 | 101.4142
2005-12-16 | 20:59 | 83 | 5.9 | -30.1 | 66 | 452 | 682.2 | 435 | -16.5063 | 99.556
2005-12-16 | 21:59 | 105 | 3.7 | -27.4 | 66 | 359 | 681.8 | 406 | -14.7125 | 93.8161
2005-12-16 | 22:59 | 99 | 10.9 | -27.4 | 65 | 382 | 681.3 | 371 | -15.8063 | 85.2286
2005-12-16 | 23:59 | 90 | 7.3 | -28.3 | 65 | 379 | 680.9 | 382 | -16.3625 | 87.4938
2005-12-17 | 0:59 | 80 | 6 | -28.6 | 65 | 405 | 680.6 | 411 | -15.7562 | 94.443
2005-12-17 | 1:59 | 75 | 6.8 | -29.3 | 65 | 461 | 680.3 | 447 | -15.3313 | 102.9494
2005-12-17 | 2:59 | 93 | 7.9 | -29.6 | 64 | 461 | 679.9 | 461 | -15.1937 | 106.2519
2005-12-17 | 3:59 | 77 | 7.6 | -29.8 | 66 | 461 | 679.6 | 451 | -15.7063 | 103.6623
2005-12-17 | 4:59 | 54 | 8.5 | -28.7 | 67 | 461 | 679.5 | 461 | -14.2937 | 106.763
2005-12-17 | 5:59 | 70 | 7.4 | -29 | 67 | 433 | 679.3 | 294 | -19.8125 | 66.0886
2005-12-17 | 6:59 | 79 | 7 | -27.5 | 67 | 438 | 679.2 | 393 | -15.2188 | 90.567
2005-12-17 | 7:59 | 86 | 8.6 | -28.2 | 65 | 461 | 679 | 452 | -14.075 | 104.8005
2005-12-17 | 8:59 | 74 | 8.5 | -28.4 | 65 | 461 | 678.8 | 458 | -14.0875 | 106.1846
2005-12-17 | 9:59 | 66 | 7.8 | -28.7 | 66 | 461 | 678.6 | 461 | -14.2937 | 106.763
2005-12-17 | 10:59 | 69 | 7.2 | -28.7 | 66 | 461 | 678.4 | 461 | -14.2937 | 106.763
2005-12-17 | 11:59 | 71 | 7.1 | -28.5 | 66 | 447 | 678.2 | 455 | -14.2812 | 105.3805
2005-12-17 | 12:59 | 74 | 7.2 | -28.9 | 66 | 453 | 678.2 | 453 | -14.7438 | 104.6592
2005-12-17 | 13:59 | 67 | 6.4 | -28.9 | 67 | 450 | 678.1 | 452 | -14.775 | 104.4107
2005-12-17 | 14:59 | 77 | 5.9 | -29 | 67 | 445 | 678 | 447 | -15.0312 | 103.1146
2005-12-17 | 15:59 | 66 | 7.9 | -29 | 68 | 441 | 677.9 | 443 | -15.1562 | 102.1237
2005-12-17 | 16:59 | 56 | 7.2 | -28.8 | 68 | 439 | 677.8 | 440 | -15.05 | 101.4897
2005-12-17 | 17:59 | 66 | 5.5 | -29.1 | 68 | 440 | 677.8 | 440 | -15.35 | 101.3271
2005-12-17 | 18:59 | 52 | 5.7 | -29.1 | 68 | 450 | 678 | 443 | -15.2562 | 102.0691
2005-12-17 | 19:59 | 57 | 4.4 | -29.2 | 68 | 386 | 678.1 | 424 | -15.95 | 97.329
2005-12-17 | 20:59 | 28 | 5.6 | -29.1 | 69 | 446 | 678.2 | 413 | -16.1938 | 94.68
2005-12-17 | 21:59 | 2 | 4.7 | -27.7 | 70 | 460 | 678.4 | 433 | -14.1687 | 100.3452
2005-12-17 | 22:59 | 348 | 5.8 | -26.5 | 74 | 332 | 678.7 | 404 | -13.875 | 93.7708
2005-12-17 | 23:59 | 342 | 4.3 | -26.6 | 74 | 335 | 678.8 | 348 | -15.725 | 79.9797
2005-12-18 | 0:59 | 349 | 2.5 | -26 | 73 | 321 | 679 | 322 | -15.9375 | 73.9199
2005-12-18 | 1:59 | 322 | 9 | -26.4 | 73 | 325 | 679.2 | 320 | -16.4 | 73.2785
2005-12-18 | 2:59 | 351 | 10.6 | -27.2 | 72 | 353 | 679.2 | 335 | -16.7312 | 76.5767
2005-12-18 | 3:59 | 325 | 11.2 | -27.4 | 71 | 362 | 679.6 | 346 | -16.5875 | 79.1524
2005-12-18 | 4:59 | 327 | 9.6 | -27.6 | 71 | 377 | 679.9 | 377 | -15.8187 | 86.6012
2005-12-18 | 5:59 | 336 | 8.8 | -27.8 | 70 | 354 | 680.1 | 357 | -16.6438 | 81.6441
2005-12-18 | 6:59 | 306 | 10.4 | -28 | 68 | 339 | 680.4 | 359 | -16.7812 | 82.0407
2005-12-18 | 7:59 | 314 | 10.1 | -28.3 | 65 | 340 | 680.6 | 348 | -17.425 | 79.2509
2005-12-18 | 8:59 | 312 | 8.4 | -28.9 | 65 | 461 | 680.9 | 409 | -16.1187 | 93.8008
2005-12-18 | 9:59 | 323 | 6.4 | -30 | 67 | 461 | 681.1 | 429 | -16.5938 | 98.1365
2005-12-18 | 10:59 | 344 | 6 | -30.6 | 66 | 461 | 681.1 | 459 | -16.2563 | 105.1901
2005-12-18 | 11:59 | 338 | 7.2 | -30.7 | 66 | 461 | 681.3 | 461 | -16.2937 | 105.6271
2005-12-18 | 12:59 | 346 | 6.9 | -30.9 | 65 | 457 | 681.6 | 452 | -16.775 | 103.297
2005-12-18 | 13:59 | 346 | 6.1 | -30.8 | 66 | 455 | 681.7 | 457 | -16.5188 | 104.5839
2005-12-18 | 14:59 | 0 | 4.9 | -31 | 66 | 448 | 681.8 | 450 | -16.9375 | 102.7498
2005-12-18 | 15:59 | 0 | 5.1 | -31.1 | 66 | 447 | 681.9 | 447 | -17.1313 | 101.9582
2005-12-18 | 16:59 | 0 | 6.1 | -30.7 | 66 | 452 | 681.9 | 447 | -16.7312 | 102.1784
2005-12-18 | 17:59 | 9 | 3.7 | -31.3 | 66 | 452 | 682.2 | 439 | -17.5813 | 99.89
2005-12-18 | 18:59 | 14 | 4.8 | -31.3 | 66 | 456 | 682.4 | 452 | -17.175 | 103.0743
2005-12-18 | 19:59 | 25 | 3.3 | -31.6 | 67 | 461 | 682.5 | 426 | -18.2875 | 96.5613
2005-12-18 | 20:59 | 72 | 3.6 | -32.4 | 66 | 429 | 682.5 | 427 | -19.0562 | 96.3836
2005-12-18 | 21:59 | 69 | 3.8 | -32.7 | 66 | 448 | 682.5 | 443 | -18.8562 | 100.1043
2005-12-18 | 22:59 | 65 | 4.6 | -32.6 | 66 | 456 | 682.7 | 451 | -18.5063 | 102.1065
2005-12-18 | 23:59 | 74 | 4.6 | -32.1 | 66 | 391 | 682.8 | 444 | -18.225 | 100.6756
2005-12-19 | 0:59 | 79 | 4.8 | -32.3 | 66 | 461 | 682.8 | 424 | -19.05 | 95.7097
2005-12-19 | 1:59 | 75 | 5.5 | -32.4 | 66 | 461 | 682.8 | 449 | -18.3687 | 101.7298
2005-12-19 | 2:59 | 71 | 5.3 | -32.3 | 65 | 461 | 682.7 | 461 | -17.8938 | 104.7184
2005-12-19 | 3:59 | 69 | 5.1 | -32.6 | 66 | 447 | 682.6 | 457 | -18.3188 | 103.5705
2005-12-19 | 4:59 | 64 | 5.4 | -32.3 | 65 | 461 | 682.7 | 456 | -18.05 | 103.4949
2005-12-19 | 5:59 | 72 | 6.3 | -32.4 | 64 | 461 | 682.7 | 301 | -22.9937 | 66.4824
2005-12-19 | 6:59 | 69 | 5.5 | -32.4 | 64 | 461 | 682.7 | 461 | -17.9937 | 104.6616
2005-12-19 | 7:59 | 68 | 6.3 | -32.3 | 64 | 457 | 682.6 | 459 | -17.9563 | 104.2288
2005-12-19 | 8:59 | 79 | 6 | -32.2 | 64 | 461 | 682.5 | 456 | -17.95 | 103.551
2005-12-19 | 9:59 | 80 | 6.3 | -32.3 | 64 | 461 | 682.3 | 461 | -17.8938 | 104.7184
2005-12-19 | 10:59 | 90 | 5.6 | -32.4 | 64 | 461 | 682.2 | 461 | -17.9937 | 104.6616
2005-12-19 | 11:59 | 98 | 5.5 | -32.3 | 63 | 461 | 682.1 | 461 | -17.8938 | 104.7184
2005-12-19 | 12:59 | 98 | 4.9 | -32.2 | 63 | 457 | 682 | 460 | -17.825 | 104.5302
2005-12-19 | 13:59 | 115 | 6.5 | -32 | 63 | 451 | 681.8 | 454 | -17.8125 | 103.1738
2005-12-19 | 14:59 | 117 | 7.7 | -31.9 | 63 | 447 | 681.4 | 449 | -17.8687 | 102.0064
2005-12-19 | 15:59 | 122 | 7.4 | -32 | 63 | 443 | 681.3 | 445 | -18.0938 | 100.9743
2005-12-19 | 16:59 | 112 | 6.9 | -32.1 | 63 | 442 | 681.1 | 442 | -18.2875 | 100.1881
2005-12-19 | 17:59 | 84 | 7.5 | -31.9 | 64 | 444 | 681.1 | 443 | -18.0562 | 100.5409
2005-12-19 | 18:59 | 78 | 6.7 | -32.2 | 64 | 452 | 681 | 446 | -18.2625 | 101.1085
2005-12-19 | 19:59 | 70 | 6.1 | -32.2 | 64 | 446 | 681 | 446 | -18.2625 | 101.1085
2005-12-19 | 20:59 | 58 | 6.6 | -32.2 | 65 | 447 | 681 | 437 | -18.5437 | 98.9167
2005-12-19 | 21:59 | 55 | 6.1 | -32.3 | 66 | 452 | 681.1 | 450 | -18.2375 | 102.0291
2005-12-19 | 22:59 | 65 | 7.7 | -32 | 66 | 457 | 680.9 | 455 | -17.7812 | 103.4185
2005-12-19 | 23:59 | 84 | 6.2 | -32.1 | 65 | 461 | 680.9 | 460 | -17.725 | 104.5869
2005-12-20 | 0:59 | 88 | 6 | -31.9 | 65 | 461 | 680.9 | 461 | -17.4937 | 104.9456
2005-12-20 | 1:59 | 86 | 6.4 | -31.9 | 64 | 461 | 680.7 | 461 | -17.4937 | 104.9456
2005-12-20 | 2:59 | 82 | 6.6 | -31.6 | 64 | 461 | 680.6 | 461 | -17.1938 | 105.116
2005-12-20 | 3:59 | 90 | 7.1 | -31.7 | 65 | 461 | 680.4 | 458 | -17.3875 | 104.3226
2005-12-20 | 4:59 | 102 | 9.2 | -31.5 | 64 | 461 | 680.3 | 461 | -17.0938 | 105.1728
2005-12-20 | 5:59 | 101 | 8.5 | -31.2 | 63 | 461 | 680.1 | 302 | -21.7625 | 67.1614
2005-12-20 | 6:59 | 94 | 7 | -31 | 63 | 461 | 680 | 461 | -16.5938 | 105.4567
2005-12-20 | 7:59 | 96 | 8.3 | -30.7 | 63 | 461 | 680 | 461 | -16.2937 | 105.6271
2005-12-20 | 8:59 | 92 | 7.9 | -30.4 | 64 | 461 | 679.7 | 458 | -16.0875 | 105.0561
2005-12-20 | 9:59 | 93 | 6.6 | -30.4 | 64 | 461 | 679.5 | 461 | -15.9938 | 105.7975
2005-12-20 | 10:59 | 87 | 8 | -30 | 64 | 461 | 679.4 | 461 | -15.5938 | 106.0247
2005-12-20 | 11:59 | 85 | 8.1 | -30 | 64 | 461 | 679.4 | 461 | -15.5938 | 106.0247
2005-12-20 | 12:59 | 86 | 7.6 | -30 | 64 | 456 | 679.3 | 459 | -15.6562 | 105.5294
2005-12-20 | 13:59 | 86 | 8.4 | -29.9 | 64 | 451 | 679.1 | 454 | -15.7125 | 104.3484
2005-12-20 | 14:59 | 88 | 8 | -30 | 64 | 447 | 678.9 | 449 | -15.9688 | 103.0574
2005-12-20 | 15:59 | 91 | 7.7 | -30.1 | 64 | 444 | 678.7 | 445 | -16.1938 | 102.0159
2005-12-20 | 16:59 | 96 | 8.2 | -30.2 | 64 | 442 | 678.4 | 442 | -16.3875 | 101.2227
2005-12-20 | 17:59 | 89 | 7.1 | -30.2 | 65 | 442 | 678.4 | 442 | -16.3875 | 101.2227
2005-12-20 | 18:59 | 95 | 7.4 | -30.2 | 65 | 450 | 678.2 | 445 | -16.2937 | 101.9611
2005-12-20 | 19:59 | 82 | 7.5 | -30.1 | 65 | 445 | 678.2 | 445 | -16.1938 | 102.0159
2005-12-20 | 20:59 | 85 | 6.5 | -30 | 65 | 447 | 678 | 437 | -16.3438 | 100.1012
2005-12-20 | 21:59 | 87 | 6.8 | -30.1 | 65 | 454 | 678 | 443 | -16.2563 | 101.5233
2005-12-20 | 22:59 | 84 | 6.6 | -30 | 65 | 458 | 677.8 | 455 | -15.7812 | 104.5397
2005-12-20 | 23:59 | 83 | 6.1 | -30.1 | 65 | 461 | 677.8 | 458 | -15.7875 | 105.2254
2005-12-21 | 0:59 | 84 | 5.2 | -30.1 | 65 | 461 | 677.8 | 461 | -15.6937 | 105.9679
2005-12-21 | 1:59 | 78 | 6.8 | -30 | 65 | 461 | 677.8 | 461 | -15.5938 | 106.0247
2005-12-21 | 2:59 | 71 | 7.1 | -29.8 | 64 | 461 | 677.6 | 461 | -15.3938 | 106.1383
2005-12-21 | 3:59 | 72 | 6.6 | -29.8 | 65 | 461 | 677.4 | 458 | -15.4875 | 105.3947
2005-12-21 | 4:59 | 54 | 3.3 | -29.9 | 64 | 461 | 677.6 | 461 | -15.4938 | 106.0815
2005-12-21 | 5:59 | 67 | 6.2 | -29.6 | 64 | 461 | 677.5 | 303 | -20.1313 | 67.9927
2005-12-21 | 6:59 | 65 | 6.1 | -29.7 | 64 | 461 | 677.6 | 461 | -15.2937 | 106.1951
2005-12-21 | 7:59 | 53 | 6.3 | -29.6 | 63 | 461 | 677.7 | 461 | -15.1937 | 106.2519
2005-12-21 | 8:59 | 24 | 7.1 | -29.6 | 63 | 461 | 677.8 | 458 | -15.2875 | 105.5075
2005-12-21 | 9:59 | 13 | 8.6 | -29.7 | 65 | 444 | 678.1 | 459 | -15.3562 | 105.699
2005-12-21 | 10:59 | 344 | 12.7 | -28.9 | 66 | 461 | 678.5 | 421 | -15.7438 | 96.7474
2005-12-21 | 11:59 | 336 | 12.5 | -28.5 | 66 | 366 | 679 | 418 | -15.4375 | 96.2157
2005-12-21 | 12:59 | 353 | 12.8 | -28.9 | 65 | 434 | 679.2 | 435 | -15.3063 | 100.1991
2005-12-21 | 13:59 | 350 | 12.7 | -28.9 | 66 | 425 | 679.4 | 414 | -15.9625 | 95.0272
2005-12-21 | 14:59 | 345 | 11.8 | -28.9 | 65 | 334 | 679.7 | 393 | -16.6187 | 89.8892
2005-12-21 | 15:59 | 349 | 12.4 | -29.1 | 65 | 449 | 680 | 434 | -15.5375 | 99.8451
2005-12-21 | 16:59 | 5 | 8.7 | -29.6 | 65 | 444 | 680.2 | 438 | -15.9125 | 100.563
2005-12-21 | 17:59 | 18 | 9.8 | -29.8 | 66 | 443 | 680.5 | 443 | -15.9563 | 101.6871
2005-12-21 | 18:59 | 16 | 14.1 | -29.9 | 65 | 445 | 680.6 | 441 | -16.1187 | 101.1397
2005-12-21 | 19:59 | 22 | 9.8 | -29.7 | 66 | 456 | 680.8 | 430 | -16.2625 | 98.5408
2005-12-21 | 20:59 | 20 | 11.1 | -29.4 | 67 | 452 | 680.8 | 425 | -16.1187 | 97.4702
2005-12-21 | 21:59 | 14 | 10.8 | -29.1 | 67 | 423 | 680.9 | 443 | -15.2562 | 102.0691
2005-12-21 | 22:59 | 14 | 12.3 | -28.7 | 68 | 458 | 681 | 427 | -15.3562 | 98.33
2005-12-21 | 23:59 | 9 | 12.8 | -27.9 | 69 | 360 | 681.1 | 418 | -14.8375 | 96.5246
2005-12-22 | 0:59 | 11 | 10.9 | -27.4 | 68 | 362 | 681.4 | 379 | -15.5563 | 87.1832
2005-12-22 | 1:59 | 19 | 12 | -27.8 | 68 | 387 | 681.4 | 376 | -16.05 | 86.2643
2005-12-22 | 2:59 | 25 | 12.6 | -28.4 | 67 | 446 | 681.2 | 417 | -15.3688 | 96.0208
2005-12-22 | 3:59 | 24 | 11.9 | -28.5 | 67 | 461 | 681 | 447 | -14.5312 | 103.39
2005-12-22 | 4:59 | 23 | 13.2 | -28 | 67 | 461 | 681 | 449 | -13.9688 | 104.1637
2005-12-22 | 5:59 | 24 | 13.9 | -28.5 | 66 | 410 | 681 | 320 | -18.5 | 72.4506
2005-12-22 | 6:59 | 23 | 15.1 | -28.5 | 66 | 434 | 681 | 435 | -14.9062 | 100.4134
2005-12-22 | 7:59 | 27 | 14.9 | -28.2 | 66 | 425 | 681.2 | 450 | -14.1375 | 104.3022
2005-12-22 | 8:59 | 22 | 14 | -28.1 | 66 | 435 | 681.1 | 449 | -14.0687 | 104.1084
2005-12-22 | 9:59 | 27 | 15.5 | -28 | 66 | 346 | 681.1 | 441 | -14.2188 | 102.172
2005-12-22 | 10:59 | 23 | 14.9 | -28 | 66 | 461 | 681 | 437 | -14.3438 | 101.178
2005-12-22 | 11:59 | 22 | 16 | -28.3 | 66 | 372 | 681 | 436 | -14.675 | 100.7685
2005-12-22 | 12:59 | 28 | 13 | -27.9 | 67 | 407 | 681.1 | 423 | -14.6813 | 97.7607
2005-12-22 | 13:59 | 27 | 16 | -27.7 | 66 | 336 | 680.8 | 423 | -14.4812 | 97.8649
2005-12-22 | 14:59 | 30 | 16.1 | -27.8 | 67 | 434 | 680.6 | 414 | -14.8625 | 95.5882
2005-12-22 | 15:59 | 42 | 14.1 | -28.2 | 66 | 451 | 680.5 | 440 | -14.45 | 101.8149
2005-12-22 | 16:59 | 39 | 12.1 | -28.3 | 66 | 451 | 680.3 | 443 | -14.4563 | 102.5057
2005-12-22 | 17:59 | 36 | 12.7 | -28.5 | 66 | 432 | 680.2 | 434 | -14.9375 | 100.1659
2005-12-22 | 18:59 | 37 | 14.2 | -28.5 | 66 | 435 | 680.2 | 427 | -15.1562 | 98.4352
2005-12-22 | 19:59 | 39 | 8.9 | -28.9 | 66 | 447 | 680.1 | 439 | -15.1813 | 101.1881
2005-12-22 | 20:59 | 49 | 9.7 | -29.2 | 66 | 448 | 680 | 438 | -15.5125 | 100.7788
2005-12-22 | 21:59 | 49 | 8.4 | -29.6 | 65 | 452 | 679.8 | 450 | -15.5375 | 103.526
2005-12-22 | 22:59 | 61 | 8.5 | -29.6 | 64 | 457 | 679.8 | 455 | -15.3812 | 104.7639
2005-12-22 | 23:59 | 63 | 7.4 | -29.7 | 64 | 461 | 679.7 | 460 | -15.325 | 105.947
2005-12-23 | 0:59 | 53 | 5.8 | -29.8 | 64 | 461 | 679.5 | 461 | -15.3938 | 106.1383
2005-12-23 | 1:59 | 58 | 3.9 | -30 | 65 | 461 | 679.2 | 461 | -15.5938 | 106.0247
2005-12-23 | 2:59 | 53 | 5.1 | -29.9 | 64 | 461 | 679.2 | 461 | -15.4938 | 106.0815
2005-12-23 | 3:59 | 40 | 4.4 | -30.1 | 66 | 461 | 679 | 459 | -15.7562 | 105.4728
2005-12-23 | 4:59 | 22 | 3.9 | -30 | 65 | 461 | 679 | 461 | -15.5938 | 106.0247
2005-12-23 | 5:59 | 18 | 3.7 | -30 | 66 | 461 | 679.1 | 299 | -20.6562 | 66.9017
2005-12-23 | 6:59 | 18 | 3.7 | -30 | 66 | 461 | 679.1 | 461 | -15.5938 | 106.0247
2005-12-23 | 7:59 | 2 | 4.9 | -30 | 66 | 461 | 679.1 | 461 | -15.5938 | 106.0247
2005-12-23 | 8:59 | 13 | 4.7 | -30 | 66 | 461 | 679.1 | 457 | -15.7188 | 105.0344
2005-12-23 | 9:59 | 5 | 5 | -29.8 | 66 | 461 | 679 | 461 | -15.3938 | 106.1383
2005-12-23 | 10:59 | 3 | 5.7 | -29.6 | 66 | 440 | 679.1 | 456 | -15.35 | 105.0117
2005-12-23 | 11:59 | 4 | 6.4 | -29.4 | 67 | 461 | 679.2 | 456 | -15.15 | 105.1241
2005-12-23 | 12:59 | 10 | 5.8 | -29.5 | 67 | 461 | 679.2 | 456 | -15.25 | 105.0679
2005-12-23 | 13:59 | 348 | 5.1 | -29.6 | 69 | 433 | 679.2 | 432 | -16.1 | 99.0856
2005-12-23 | 14:59 | 353 | 5.5 | -29.1 | 67 | 459 | 679.1 | 445 | -15.1937 | 102.5642
2005-12-23 | 15:59 | 350 | 5.1 | -29.4 | 67 | 429 | 679.1 | 427 | -16.0562 | 97.9618
2005-12-23 | 16:59 | 0 | 5.3 | -29.3 | 67 | 424 | 679 | 436 | -15.675 | 100.2313
2005-12-23 | 17:59 | 0 | 5.2 | -29.8 | 68 | 415 | 679.2 | 414 | -16.8625 | 94.5681
2005-12-23 | 18:59 | 343 | 5.7 | -29.8 | 67 | 392 | 679.4 | 421 | -16.6438 | 96.2806
2005-12-23 | 19:59 | 332 | 6.3 | -29.2 | 68 | 453 | 679.5 | 410 | -16.3875 | 93.8943
2005-12-23 | 20:59 | 329 | 6.5 | -29.6 | 68 | 452 | 679.5 | 439 | -15.8812 | 100.8095
2005-12-23 | 21:59 | 346 | 5.7 | -30.3 | 68 | 451 | 679.7 | 447 | -16.3313 | 102.3987
2005-12-23 | 22:59 | 336 | 5 | -30 | 68 | 461 | 679.7 | 456 | -15.75 | 104.787
2005-12-23 | 23:59 | 327 | 6 | -30.4 | 68 | 433 | 679.8 | 434 | -16.8375 | 99.15
2005-12-24 | 0:59 | 325 | 6.1 | -30.2 | 69 | 442 | 679.7 | 434 | -16.6375 | 99.2569
2005-12-24 | 1:59 | 318 | 5.5 | -30.3 | 69 | 461 | 679.7 | 457 | -16.0188 | 104.8655
2005-12-24 | 2:59 | 333 | 7 | -30.5 | 69 | 461 | 679.6 | 460 | -16.125 | 105.4936
2005-12-24 | 3:59 | 341 | 5.4 | -31.1 | 69 | 440 | 679.7 | 449 | -17.0688 | 102.4489
2005-12-24 | 4:59 | 338 | 5.4 | -30.7 | 69 | 461 | 679.8 | 449 | -16.6687 | 102.6702
2005-12-24 | 5:59 | 311 | 5.9 | -29.8 | 69 | 389 | 680 | 328 | -19.55 | 73.8375
2005-12-24 | 6:59 | 0 | 5.2 | -30.5 | 67 | 461 | 680.1 | 437 | -16.8438 | 99.832
2005-12-24 | 7:59 | 341 | 5.1 | -30.9 | 67 | 461 | 680.1 | 452 | -16.775 | 103.297
2005-12-24 | 8:59 | 339 | 4.9 | -30.6 | 69 | 454 | 680.1 | 438 | -16.9125 | 100.0233
2005-12-24 | 9:59 | 333 | 3.9 | -30.6 | 68 | 392 | 680.3 | 438 | -16.9125 | 100.0233
2005-12-24 | 10:59 | 345 | 5.6 | -30.4 | 68 | 445 | 680.4 | 436 | -16.775 | 99.6405
2005-12-24 | 11:59 | 345 | 5.2 | -30.7 | 68 | 461 | 680.6 | 427 | -17.3562 | 97.2779
2005-12-24 | 12:59 | 337 | 5.1 | -31 | 68 | 422 | 680.6 | 452 | -16.875 | 103.2413
2005-12-24 | 13:59 | 358 | 5.5 | -30.9 | 68 | 445 | 680.5 | 447 | -16.9312 | 102.0683
2005-12-24 | 14:59 | 6 | 6.5 | -31.2 | 66 | 456 | 680.4 | 443 | -17.3562 | 100.923
2005-12-24 | 15:59 | 3 | 6 | -31.2 | 66 | 452 | 680.6 | 450 | -17.1375 | 102.639
2005-12-24 | 16:59 | 6 | 6.4 | -31.4 | 67 | 432 | 680.7 | 431 | -17.9312 | 97.8838
2005-12-24 | 17:59 | 353 | 6.1 | -31.3 | 67 | 411 | 680.9 | 420 | -18.175 | 95.2595
2005-12-24 | 18:59 | 0 | 5.8 | -31.3 | 67 | 419 | 680.9 | 427 | -17.9563 | 96.9623
2005-12-24 | 19:59 | 6 | 6.1 | -31.5 | 68 | 453 | 680.9 | 447 | -17.5312 | 101.7379
2005-12-24 | 20:59 | 5 | 6.6 | -31.5 | 69 | 435 | 681 | 423 | -18.2812 | 95.8846
2005-12-24 | 21:59 | 356 | 6.3 | -31.6 | 69 | 444 | 681.1 | 452 | -17.475 | 102.9072
2005-12-24 | 22:59 | 0 | 6.6 | -31.6 | 69 | 457 | 681.2 | 449 | -17.5688 | 102.1723
2005-12-24 | 23:59 | 3 | 5.5 | -31.5 | 69 | 461 | 681.2 | 461 | -17.0938 | 105.1728
2005-12-25 | 0:59 | 11 | 5.6 | -31.1 | 70 | 461 | 681.1 | 454 | -16.9125 | 103.6772
2005-12-25 | 1:59 | 14 | 4.7 | -30.4 | 70 | 461 | 681 | 453 | -16.2437 | 103.822
2005-12-25 | 2:59 | 14 | 5.1 | -31 | 70 | 386 | 681 | 428 | -17.625 | 97.364
2005-12-25 | 3:59 | 15 | 5.2 | -31.1 | 69 | 461 | 680.8 | 437 | -17.4438 | 99.509
2005-12-25 | 4:59 | 13 | 4.9 | -31.1 | 68 | 461 | 680.7 | 461 | -16.6938 | 105.4
2005-12-25 | 5:59 | 28 | 3.8 | -31.1 | 67 | 461 | 680.6 | 322 | -21.0375 | 71.8967
2005-12-25 | 6:59 | 72 | 2.8 | -31.4 | 66 | 461 | 680.7 | 455 | -17.1812 | 103.7549
2005-12-25 | 7:59 | 78 | 2.9 | -31.9 | 66 | 452 | 680.7 | 460 | -17.525 | 104.7002
2005-12-25 | 8:59 | 77 | 3.2 | -32.1 | 65 | 461 | 680.6 | 453 | -17.9438 | 102.8733
2005-12-25 | 9:59 | 81 | 4.2 | -32.4 | 65 | 458 | 680.5 | 454 | -18.2125 | 102.95
2005-12-25 | 10:59 | 75 | 4.5 | -32.1 | 65 | 461 | 680.4 | 446 | -18.1625 | 101.1634
2005-12-25 | 11:59 | 68 | 3.5 | -32.1 | 65 | 447 | 680.2 | 442 | -18.2875 | 100.1881
2005-12-25 | 12:59 | 56 | 4.7 | -32.4 | 65 | 447 | 680.1 | 449 | -18.3687 | 101.7298
2005-12-25 | 13:59 | 62 | 4.7 | -32.5 | 65 | 427 | 680 | 446 | -18.5625 | 100.9436
2005-12-25 | 14:59 | 66 | 3.8 | -32.7 | 65 | 455 | 679.8 | 447 | -18.7312 | 101.077
2005-12-25 | 15:59 | 49 | 3.4 | -32.9 | 66 | 443 | 679.6 | 439 | -19.1812 | 99.0247
2005-12-25 | 16:59 | 50 | 3.1 | -32.7 | 66 | 448 | 679.7 | 435 | -19.1062 | 98.1626
2005-12-25 | 17:59 | 21 | 3.5 | -32.8 | 66 | 460 | 679.6 | 439 | -19.0813 | 99.0787
2005-12-25 | 18:59 | 10 | 5.3 | -32.3 | 67 | 449 | 679.6 | 450 | -18.2375 | 102.0291
2005-12-25 | 19:59 | 1 | 4.8 | -32.2 | 67 | 438 | 679.8 | 452 | -18.075 | 102.5731
2005-12-26 | 2:59 | 1 | 5.5 | -32.5 | 67 | 461 | 680 | 461 | -18.0938 | 104.6048
2005-12-26 | 3:59 | 353 | 5.5 | -32.9 | 67 | 439 | 680 | 453 | -18.7437 | 102.4268
2005-12-26 | 4:59 | 0 | 4.8 | -32.8 | 67 | 461 | 680.2 | 459 | -18.4563 | 103.946
2005-12-26 | 5:59 | 4 | 5 | -32.6 | 67 | 461 | 680.3 | 295 | -23.3813 | 65.0163
2005-12-26 | 6:59 | 8 | 4.8 | -32.6 | 66 | 461 | 680.5 | 461 | -18.1938 | 104.548
2005-12-26 | 7:59 | 11 | 5.8 | -32.4 | 66 | 458 | 680.6 | 460 | -18.025 | 104.4169
2005-12-26 | 8:59 | 12 | 5.4 | -32.3 | 66 | 461 | 680.7 | 453 | -18.1438 | 102.7616
2005-12-26 | 9:59 | 19 | 4.2 | -32.2 | 66 | 461 | 680.8 | 456 | -17.95 | 103.551
2005-12-26 | 10:59 | 46 | 3.8 | -32.4 | 66 | 461 | 681 | 460 | -18.025 | 104.4169
2005-12-26 | 11:59 | 36 | 4.3 | -32.3 | 66 | 453 | 681.1 | 451 | -18.2063 | 102.2732
2005-12-26 | 12:59 | 42 | 3.4 | -32.3 | 66 | 446 | 681.1 | 453 | -18.1438 | 102.7616
2005-12-26 | 13:59 | 38 | 5.2 | -32 | 66 | 461 | 681.1 | 450 | -17.9375 | 102.1954
2005-12-26 | 14:59 | 58 | 4 | -32.3 | 66 | 415 | 681 | 434 | -18.7375 | 98.1341
2005-12-26 | 15:59 | 45 | 5.2 | -32 | 66 | 422 | 681 | 429 | -18.5938 | 97.0795
2005-12-26 | 16:59 | 53 | 4.4 | -32.3 | 66 | 433 | 681.2 | 430 | -18.8625 | 97.1634
2005-12-26 | 17:59 | 43 | 4.4 | -33.2 | 65 | 442 | 681.3 | 414 | -20.2625 | 92.834
2005-12-26 | 18:59 | 29 | 6.8 | -32 | 66 | 362 | 681.4 | 411 | -19.1562 | 92.7214
2005-12-26 | 19:59 | 34 | 5 | -31.2 | 67 | 399 | 681.7 | 381 | -19.2937 | 85.8889
2005-12-26 | 20:59 | 29 | 6 | -31.2 | 67 | 449 | 681.8 | 431 | -17.7312 | 97.99
2005-12-26 | 21:59 | 19 | 5.7 | -31.8 | 67 | 461 | 681.8 | 438 | -18.1125 | 99.3758
2005-12-26 | 22:59 | 13 | 4.5 | -31.8 | 67 | 461 | 682.1 | 457 | -17.5188 | 104.0209
2005-12-26 | 23:59 | 0 | 4 | -32 | 67 | 448 | 682.1 | 443 | -18.1562 | 100.4864
2005-12-27 | 0:59 | 343 | 4.2 | -32.1 | 66 | 461 | 682.3 | 456 | -17.85 | 103.6072
2005-12-27 | 1:59 | 331 | 5.1 | -32.3 | 66 | 461 | 682.3 | 460 | -17.925 | 104.4735
2005-12-27 | 2:59 | 338 | 4.4 | -32.8 | 66 | 461 | 682.4 | 452 | -18.675 | 102.239
2005-12-27 | 3:59 | 332 | 5.1 | -33.1 | 67 | 461 | 682.5 | 459 | -18.7563 | 103.7764
2005-12-27 | 4:59 | 318 | 4 | -33 | 67 | 461 | 682.7 | 460 | -18.625 | 104.0768
2005-12-27 | 5:59 | 292 | 4.4 | -32.7 | 67 | 431 | 683 | 301 | -23.2937 | 66.3711
2005-12-27 | 6:59 | 296 | 4.5 | -32.8 | 67 | 461 | 683.4 | 452 | -18.675 | 102.239
2005-12-27 | 7:59 | 286 | 5.7 | -32.4 | 68 | 445 | 683.7 | 460 | -18.025 | 104.4169
2005-12-27 | 8:59 | 300 | 4.9 | -32.4 | 68 | 461 | 684 | 454 | -18.2125 | 102.95
2005-12-27 | 9:59 | 309 | 4.5 | -32.3 | 67 | 461 | 684.4 | 458 | -17.9875 | 103.984
2005-12-27 | 10:59 | 290 | 6.5 | -32.3 | 68 | 461 | 684.6 | 451 | -18.2063 | 102.2732
2005-12-27 | 11:59 | 319 | 4.7 | -32.9 | 66 | 461 | 684.9 | 453 | -18.7437 | 102.4268
2005-12-27 | 12:59 | 312 | 5.3 | -32.4 | 66 | 444 | 685.2 | 434 | -18.8375 | 98.0806
2005-12-27 | 13:59 | 314 | 3 | -32.8 | 65 | 453 | 685.5 | 450 | -18.7375 | 101.7519
2005-12-27 | 14:59 | 279 | 4 | -32.8 | 65 | 458 | 685.7 | 448 | -18.8 | 101.2652
2005-12-27 | 15:59 | 280 | 4.6 | -32.8 | 65 | 385 | 686 | 441 | -19.0188 | 99.5641
2005-12-27 | 16:59 | 275 | 4.7 | -32.9 | 65 | 303 | 686.5 | 409 | -20.1187 | 91.7852
2005-12-27 | 17:59 | 289 | 4.1 | -32.7 | 65 | 426 | 686.9 | 427 | -19.3562 | 96.2258
2005-12-27 | 18:59 | 307 | 5.2 | -32.7 | 66 | 458 | 687.3 | 443 | -18.8562 | 100.1043
2005-12-27 | 19:59 | 282 | 5.1 | -32.8 | 66 | 444 | 687.6 | 443 | -18.9563 | 100.0497
2005-12-27 | 20:59 | 288 | 7.7 | -32.9 | 66 | 443 | 687.8 | 435 | -19.3062 | 98.0554
2005-12-27 | 21:59 | 284 | 7.3 | -33.1 | 66 | 450 | 688.1 | 448 | -19.1 | 101.0996
2005-12-27 | 22:59 | 283 | 6.7 | -33 | 66 | 461 | 688.4 | 452 | -18.875 | 102.1276
2005-12-27 | 23:59 | 285 | 6.3 | -33 | 66 | 459 | 688.8 | 449 | -18.9688 | 101.3979
2005-12-28 | 0:59 | 294 | 5.8 | -33 | 66 | 461 | 688.8 | 459 | -18.6562 | 103.8329
2005-12-28 | 1:59 | 293 | 6.2 | -33 | 67 | 461 | 689 | 456 | -18.75 | 103.1016
2005-12-28 | 2:59 | 308 | 5.2 | -33 | 66 | 435 | 689.2 | 455 | -18.7812 | 102.858
2005-12-28 | 3:59 | 316 | 6.4 | -32.7 | 67 | 461 | 689.2 | 446 | -18.7625 | 100.8337
2005-12-28 | 4:59 | 320 | 7.9 | -32.1 | 66 | 368 | 689.4 | 436 | -18.475 | 98.7273
2005-12-28 | 5:59 | 333 | 7.3 | -32 | 65 | 461 | 689.6 | 332 | -21.625 | 73.8893
2005-12-28 | 6:59 | 329 | 9 | -32 | 65 | 438 | 689.7 | 440 | -18.25 | 99.755
2005-12-28 | 7:59 | 312 | 11.1 | -31.6 | 65 | 461 | 689.8 | 437 | -17.9438 | 99.2398
2005-12-28 | 8:59 | 315 | 9.5 | -31.8 | 65 | 461 | 690.1 | 433 | -18.2688 | 98.158
2005-12-28 | 9:59 | 307 | 9.8 | -31.9 | 66 | 407 | 690 | 430 | -18.4625 | 97.3753
2005-12-28 | 10:59 | 311 | 9.4 | -31.8 | 65 | 438 | 690.2 | 403 | -19.2063 | 90.8918
2005-12-28 | 11:59 | 313 | 8.1 | -31.9 | 65 | 453 | 690.3 | 446 | -17.9625 | 101.2733
2005-12-28 | 12:59 | 320 | 7.4 | -31.8 | 64 | 461 | 690.4 | 451 | -17.7063 | 102.551
2005-12-28 | 13:59 | 307 | 10 | -31.5 | 66 | 461 | 690.4 | 410 | -18.6875 | 92.7326
2005-12-28 | 14:59 | 309 | 10.3 | -31.6 | 65 | 405 | 690.3 | 440 | -17.85 | 99.9719
2005-12-28 | 15:59 | 310 | 8.3 | -31.7 | 65 | 324 | 690.4 | 423 | -18.4812 | 95.7804
2005-12-28 | 16:59 | 305 | 9 | -31.4 | 66 | 406 | 690.4 | 411 | -18.5562 | 93.0252
2005-12-28 | 17:59 | 309 | 9.3 | -31.1 | 65 | 422 | 690.6 | 395 | -18.7563 | 89.3065
2005-12-28 | 18:59 | 306 | 10.1 | -31.1 | 64 | 372 | 690.7 | 421 | -17.9438 | 95.6063
2005-12-28 | 19:59 | 300 | 8.4 | -31.3 | 65 | 345 | 690.7 | 436 | -17.675 | 99.157
2005-12-28 | 20:59 | 304 | 9.2 | -31.3 | 65 | 429 | 690.7 | 408 | -18.55 | 92.3493
2005-12-28 | 21:59 | 304 | 8.8 | -31.2 | 65 | 453 | 690.8 | 431 | -17.7312 | 97.99
2005-12-28 | 22:59 | 312 | 8.3 | -31.9 | 66 | 346 | 690.7 | 384 | -19.9 | 86.2783
2005-12-28 | 23:59 | 294 | 9 | -30.8 | 66 | 402 | 690.4 | 366 | -19.3625 | 82.4764
2005-12-29 | 0:59 | 295 | 8.6 | -30.2 | 66 | 332 | 690.3 | 355 | -19.1062 | 80.1097
2005-12-29 | 1:59 | 289 | 8.7 | -29.3 | 67 | 370 | 690.1 | 346 | -18.4875 | 78.3425
2005-12-29 | 2:59 | 287 | 11 | -29 | 67 | 424 | 690 | 396 | -16.625 | 90.5723
2005-12-29 | 3:59 | 293 | 9.7 | -28.9 | 67 | 384 | 689.7 | 401 | -16.3687 | 91.8425
2005-12-29 | 4:59 | 285 | 8.2 | -28.7 | 68 | 418 | 689.5 | 396 | -16.325 | 90.7187
2005-12-29 | 5:59 | 286 | 7.8 | -28.1 | 68 | 392 | 689.5 | 421 | -14.9437 | 97.1623
2005-12-29 | 6:59 | 279 | 6 | -28.4 | 68 | 409 | 689.4 | 365 | -16.9937 | 83.3163
2005-12-29 | 7:59 | 270 | 4.7 | -28.1 | 68 | 403 | 689.4 | 408 | -15.35 | 93.9578
2005-12-29 | 8:59 | 288 | 5.2 | -28.3 | 68 | 375 | 689.4 | 381 | -16.3938 | 87.2501
2005-12-29 | 9:59 | 279 | 3.7 | -28.3 | 69 | 323 | 689.2 | 347 | -17.4563 | 79.0098
2005-12-29 | 10:59 | 293 | 3.3 | -28.8 | 69 | 332 | 689 | 335 | -18.3313 | 75.9163
2005-12-29 | 11:59 | 339 | 3.9 | -28.7 | 68 | 426 | 688.9 | 422 | -15.5125 | 97.0974
2005-12-29 | 12:59 | 330 | 3.7 | -28.6 | 68 | 409 | 688.8 | 444 | -14.725 | 102.5901
2005-12-29 | 13:59 | 337 | 4.7 | -29.1 | 68 | 386 | 688.6 | 384 | -17.1 | 87.603
2005-12-29 | 14:59 | 322 | 3.9 | -29 | 68 | 416 | 688.6 | 417 | -15.9688 | 95.7126
2005-12-29 | 15:59 | 348 | 5.4 | -29.4 | 67 | 437 | 688.7 | 430 | -15.9625 | 98.6997
2005-12-29 | 16:59 | 344 | 6 | -29.1 | 67 | 461 | 688.4 | 435 | -15.5062 | 100.0919
2005-12-29 | 17:59 | 352 | 6.3 | -29.1 | 68 | 451 | 688.3 | 451 | -15.0062 | 104.0512
2005-12-29 | 18:59 | 345 | 5.9 | -29.7 | 68 | 388 | 688.4 | 394 | -17.3875 | 89.7448
2005-12-29 | 19:59 | 343 | 8.2 | -29.6 | 69 | 420 | 688.2 | 351 | -18.6313 | 79.4125
2005-12-29 | 20:59 | 339 | 8.9 | -29.2 | 68 | 401 | 688.2 | 401 | -16.6687 | 91.6943
2005-12-29 | 21:59 | 339 | 8.6 | -29.4 | 67 | 384 | 688 | 351 | -18.4312 | 79.4989
2005-12-29 | 22:59 | 330 | 7.5 | -29.1 | 67 | 380 | 688 | 414 | -16.1625 | 94.9251
2005-12-29 | 23:59 | 335 | 8.2 | -29.4 | 67 | 318 | 687.7 | 386 | -17.3375 | 87.9463
2005-12-30 | 0:59 | 329 | 8.7 | -29.4 | 67 | 359 | 687.5 | 331 | -19.0562 | 74.7142
2005-12-30 | 1:59 | 316 | 8.9 | -29.3 | 67 | 348 | 687.3 | 337 | -18.7688 | 76.1879
2005-12-30 | 2:59 | 317 | 9.4 | -28.9 | 67 | 352 | 687.1 | 347 | -18.0562 | 78.7533
2005-12-30 | 3:59 | 318 | 10.3 | -28.5 | 67 | 341 | 686.9 | 341 | -17.8438 | 77.4808
2005-12-30 | 4:59 | 324 | 8.9 | -28.4 | 66 | 331 | 686.9 | 330 | -18.0875 | 74.8823
2005-12-30 | 5:59 | 316 | 8.7 | -28.3 | 67 | 322 | 686.9 | 321 | -18.2688 | 72.7684
2005-12-30 | 6:59 | 316 | 9.4 | -28.2 | 66 | 365 | 686.8 | 342 | -17.5125 | 77.8476
2005-12-30 | 7:59 | 308 | 9.3 | -28.2 | 66 | 356 | 686.6 | 367 | -16.7312 | 83.8915
2005-12-30 | 8:59 | 318 | 8.3 | -28.2 | 66 | 340 | 686.7 | 354 | -17.1375 | 80.7427
2005-12-30 | 9:59 | 311 | 9.1 | -28.2 | 67 | 316 | 686.5 | 325 | -18.0437 | 73.7653
2005-12-30 | 10:59 | 307 | 8 | -28.4 | 67 | 265 | 686.6 | 293 | -19.2437 | 66.0691
2005-12-30 | 11:59 | 326 | 9 | -28.5 | 66 | 461 | 686.5 | 399 | -16.0312 | 91.5504
2005-12-30 | 12:59 | 328 | 8.8 | -29.1 | 66 | 452 | 686.5 | 455 | -14.8812 | 105.0442
2005-12-30 | 13:59 | 327 | 5.6 | -29.6 | 66 | 447 | 686.4 | 450 | -15.5375 | 103.526
2005-12-30 | 14:59 | 315 | 5.5 | -29.5 | 67 | 443 | 686.7 | 445 | -15.5938 | 102.3449
2005-12-30 | 15:59 | 330 | 6.9 | -29.5 | 67 | 453 | 686.6 | 443 | -15.6562 | 101.8508
2005-12-30 | 16:59 | 330 | 6.6 | -29.7 | 68 | 382 | 686.7 | 409 | -16.9187 | 93.3976
2005-12-30 | 17:59 | 315 | 5.8 | -29.2 | 69 | 432 | 686.9 | 397 | -16.7937 | 90.7185
2005-12-30 | 18:59 | 337 | 6.8 | -29.3 | 69 | 322 | 686.8 | 369 | -17.7688 | 83.877
2005-12-30 | 19:59 | 328 | 8 | -28.8 | 70 | 391 | 687.1 | 395 | -16.4563 | 90.4257
2005-12-30 | 20:59 | 332 | 7.8 | -28.4 | 69 | 320 | 687.2 | 354 | -17.3375 | 80.6554
2005-12-30 | 21:59 | 323 | 12.3 | -28 | 69 | 337 | 687.3 | 337 | -17.4688 | 76.7277
2005-12-30 | 22:59 | 309 | 12 | -27.6 | 68 | 347 | 687.2 | 324 | -17.475 | 73.7653
2005-12-30 | 23:59 | 303 | 14.9 | -27.2 | 68 | 348 | 687.2 | 325 | -17.0437 | 74.1657
2005-12-31 | 0:59 | 311 | 14.2 | -26.8 | 68 | 329 | 687.4 | 346 | -15.9875 | 79.4082
2005-12-31 | 1:59 | 307 | 11 | -26.6 | 68 | 365 | 687.3 | 346 | -15.7875 | 79.4934
2005-12-31 | 2:59 | 297 | 13.9 | -26.6 | 69 | 302 | 687.3 | 328 | -16.35 | 75.1306
2005-12-31 | 3:59 | 302 | 15.5 | -26.2 | 69 | 345 | 687.5 | 323 | -16.1062 | 74.0823
2005-12-31 | 4:59 | 302 | 14.2 | -26.1 | 69 | 400 | 687.6 | 362 | -14.7875 | 83.6154
2005-12-31 | 5:59 | 300 | 13.3 | -26.3 | 70 | 293 | 687.9 | 335 | -15.8313 | 76.9481
2005-12-31 | 6:59 | 288 | 11.1 | -26.4 | 70 | 433 | 688.1 | 312 | -16.65 | 71.3504
2005-12-31 | 7:59 | 289 | 10.7 | -26.4 | 69 | 461 | 688.4 | 460 | -12.025 | 107.8172
2005-12-31 | 8:59 | 286 | 13.1 | -25.9 | 69 | 461 | 688.3 | 458 | -11.5875 | 107.5953
2005-12-31 | 9:59 | 284 | 11 | -25.9 | 69 | 394 | 688.6 | 426 | -12.5875 | 99.5529
2005-12-31 | 10:59 | 276 | 11.2 | -25.1 | 70 | 440 | 688.9 | 425 | -11.8187 | 99.7217
2005-12-31 | 11:59 | 251 | 7.6 | -24.5 | 68 | 343 | 689 | 372 | -12.875 | 86.8017
2005-12-31 | 12:59 | 251 | 6.2 | -24.9 | 69 | 454 | 689.4 | 405 | -12.2438 | 94.8169
2005-12-31 | 13:59 | 247 | 7.8 | -24.6 | 69 | 424 | 689.7 | 388 | -12.475 | 90.7264
2005-12-31 | 14:59 | 242 | 8.5 | -24.8 | 69 | 388 | 689.7 | 408 | -12.05 | 95.6166
2005-12-31 | 15:59 | 255 | 5.8 | -25.2 | 69 | 415 | 689.9 | 393 | -12.9187 | 91.6807
2005-12-31 | 16:59 | 252 | 4.7 | -24.5 | 69 | 461 | 690.4 | 418 | -11.4375 | 98.2756
2005-12-31 | 17:59 | 218 | 7.4 | -23.2 | 68 | 346 | 690.7 | 350 | -12.2625 | 81.9324
2005-12-31 | 18:59 | 216 | 6.9 | -22.7 | 69 | 359 | 690.9 | 387 | -10.6062 | 91.3835
2005-12-31 | 19:59 | 205 | 5.4 | -22.8 | 70 | 428 | 691 | 311 | -13.0813 | 72.4891
2005-12-31 | 20:59 | 192 | 7.5 | -23.9 | 69 | 435 | 691.3 | 361 | -12.6188 | 84.349
2005-12-31 | 21:59 | 187 | 4.6 | -22.5 | 70 | 336 | 691.7 | 375 | -10.7812 | 88.4691
2005-12-31 | 22:59 | 161 | 4.7 | -21.9 | 71 | 333 | 691.7 | 352 | -10.9 | 82.9915
2005-12-31 | 23:59 | 117 | 2.9 | -21.5 | 71 | 323 | 691.9 | 325 | -11.3438 | 76.448
[6 empty] | 461 |  | 461 |  | 242855.2953

## Shipping
$/lb
Vessel From PH to McMurdo | 0.21
Fly From McMurdo To NPX | 0.82
Total Shipping | 1.03